## Complete Map
Fronius Gen24 Primo/Symo Inverter Register Map with Float Inverter Model for US use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Primo GEN24 6.0 Primo GEN24 10.0 Primo GEN24 10.0 208-240 Primo GEN24 3.0 Primo GEN24 3.6 Primo GEN24 3.8 208-240 Primo GEN24 4.0 Primo GEN24 4.6 Primo GEN24 5.0 Primo GEN24 6.0 208-240 Symo GEN24 10.0 Symo GEN24 3.0 Symo GEN24 4.0 Symo GEN24 5.0 Symo GEN24 6.0 Symo GEN24 8.0
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (11x) | uint16 |  |  | 111, 113
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (11x) | uint16 | Registers |  | 60
40072 | 40073 | 2 | R | 0x03 | A | AC Current | float32 | A
40074 | 40075 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
40076 | 40077 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
40078 | 40079 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
40080 | 40081 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40082 | 40083 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40084 | 40085 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40086 | 40087 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
40088 | 40089 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40090 | 40091 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40092 | 40093 | 2 | R | 0x03 | W | AC Power | float32 | W
40094 | 40095 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
40096 | 40097 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
40098 | 40099 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
40100 | 40101 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
40102 | 40103 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
40104 | 40105 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40106 | 40107 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40108 | 40109 | 2 | R | 0x03 | DCW | DC Power | float32 | W
40110 | 40111 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
40112 | 40113 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
40114 | 40115 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
40116 | 40117 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
40118 | 40118 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40119 | 40119 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40120 | 40121 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40122 | 40123 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40124 | 40125 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40126 | 40127 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40128 | 40129 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40130 | 40131 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40132 | 40132 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40133 | 40133 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40134 | 40134 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
40135 | 40135 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40136 | 40136 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40137 | 40137 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40138 | 40138 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40139 | 40139 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40140 | 40140 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
40141 | 40141 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
40142 | 40142 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40143 | 40143 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40144 | 40144 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40145 | 40145 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40146 | 40146 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40147 | 40147 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
40148 | 40148 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
40149 | 40149 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40150 | 40150 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40151 | 40151 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
40152 | 40152 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
40153 | 40153 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40154 | 40154 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40155 | 40155 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
40156 | 40156 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
40157 | 40157 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
40158 | 40158 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
40159 | 40159 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40160 | 40160 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40161 | 40161 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40162 | 40162 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40163 | 40163 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40164 | 40164 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40165 | 40165 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40166 | 40166 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40167 | 40167 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40168 | 40168 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40169 | 40169 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40170 | 40170 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40171 | 40171 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40172 | 40172 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40173 | 40173 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40174 | 40174 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40175 | 40175 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40176 | 40176 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40177 | 40177 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40178 | 40178 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40180 | 40180 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40181 | 40181 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40182 | 40182 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40183 | 40183 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40184 | 40184 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40185 | 40185 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40186 | 40186 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40187 | 40187 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40188 | 40188 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40189 | 40189 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40190 | 40190 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40191 | 40191 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40192 | 40192 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40193 | 40193 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40194 | 40194 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40195 | 40195 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40196 | 40196 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40197 | 40200 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40201 | 40204 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40205 | 40208 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40209 | 40212 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40213 | 40216 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40217 | 40220 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40221 | 40221 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40222 | 40222 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40223 | 40223 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40224 | 40224 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40225 | 40226 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40227 | 40228 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40229 | 40232 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40233 | 40234 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40235 | 40235 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40236 | 40236 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40237 | 40237 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40238 | 40238 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40239 | 40239 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40243 | 40243 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40245 | 40245 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40249 | 40249 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40251 | 40251 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40252 | 40252 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40253 | 40253 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40254 | 40254 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40255 | 40255 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40256 | 40256 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40257 | 40257 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40258 | 40258 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40259 | 40259 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40260 | 40260 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40261 | 40261 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40262 | 40262 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40263 | 40263 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40264 | 40264 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40265 | 40265 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 48
40266 | 40266 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40267 | 40267 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40268 | 40268 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40269 | 40269 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40270 | 40271 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40272 | 40272 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 2 MPPT => 2 repeating blocks
40273 | 40273 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40274 | 40274 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40275 | 40282 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40283 | 40283 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40284 | 40284 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40285 | 40285 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40286 | 40287 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40288 | 40289 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40290 | 40290 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40291 | 40291 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40292 | 40293 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
40294 | 40294 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
40295 | 40302 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40303 | 40303 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
40304 | 40304 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
40305 | 40305 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
40306 | 40307 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40308 | 40309 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40310 | 40310 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
40311 | 40311 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
40312 | 40313 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40314 | 40314 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
40315 | 40315 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
40316 | 40316 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
40317 | 40317 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
40318 | 40318 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
40319 | 40319 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
40320 | 40321 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
40322 | 40323 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
40324 | 40324 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
40325 | 40325 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
40326 | 40326 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
40327 | 40327 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
40328 | 40328 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
40329 | 40329 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
40330 | 40330 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
40331 | 40332 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
40333 | 40336 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
40337 | 40340 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
40341 | 40344 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
40345 | 40348 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
40349 | 40349 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
40350 | 40350 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
40351 | 40351 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
40352 | 40352 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40353 | 40353 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
40354 | 40354 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
40355 | 40355 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
40356 | 40356 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
40357 | 40357 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
40358 | 40358 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
40359 | 40359 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
40360 | 40360 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
40361 | 40361 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
40362 | 40365 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
40366 | 40369 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
40370 | 40373 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
40374 | 40377 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
40378 | 40378 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
40379 | 40379 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
40380 | 40380 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
40381 | 40381 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
40382 | 40382 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
40383 | 40383 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
40384 | 40384 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
40385 | 40388 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
40389 | 40392 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
40393 | 40396 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
40397 | 40400 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
40401 | 40401 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
40402 | 40402 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
40403 | 40403 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
40404 | 40404 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
40405 | 40405 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
40406 | 40406 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
40407 | 40407 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
40408 | 40411 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
40412 | 40415 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
40416 | 40419 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
40420 | 40423 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
40424 | 40424 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
40425 | 40426 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
40427 | 40427 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40428 | 40428 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40429 | 40429 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
40430 | 40430 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40431 | 40431 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
40432 | 40432 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
40433 | 40433 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40434 | 40434 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
40435 | 40435 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
40436 | 40436 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
40437 | 40468 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40469 | 40469 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
40470 | 40470 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
40471 | 40471 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
40472 | 40472 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
40473 | 40473 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40474 | 40474 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
40475 | 40475 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40476 | 40476 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
40477 | 40477 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
40478 | 40478 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
40479 | 40479 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40480 | 40480 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40481 | 40481 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
40482 | 40482 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
40483 | 40483 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
40484 | 40484 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
40485 | 40485 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
40486 | 40486 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
40487 | 40487 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
40488 | 40488 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
40489 | 40489 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
40490 | 40490 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
40491 | 40491 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
40492 | 40493 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
40494 | 40494 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
40495 | 40495 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
40496 | 40496 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
40497 | 40497 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
40498 | 40498 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
40499 | 40499 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
40500 | 40500 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
40501 | 40501 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
40502 | 40502 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
40503 | 40503 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
40504 | 40504 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
40505 | 40505 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
40506 | 40506 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
40507 | 40507 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40508 | 40508 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
40509 | 40509 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
40510 | 40510 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
40511 | 40511 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
40512 | 40512 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
40513 | 40513 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
40514 | 40514 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40515 | 40515 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40516 | 40516 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
40517 | 40517 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40518 | 40518 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40519 | 40519 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40520 | 40520 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40521 | 40521 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
40522 | 40522 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
40523 | 40523 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
40524 | 40524 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
40525 | 40525 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40526 | 40527 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40528 | 40529 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40530 | 40531 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
40532 | 40533 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
40534 | 40535 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
40536 | 40537 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
40538 | 40538 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
40539 | 40539 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40540 | 40540 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
40541 | 40541 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
40542 | 40542 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
40543 | 40543 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40544 | 40545 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40546 | 40547 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40548 | 40548 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
40549 | 40549 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
40550 | 40551 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
40552 | 40553 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
40554 | 40554 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
40555 | 40555 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40556 | 40556 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40557 | 40557 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
40558 | 40559 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
40560 | 40561 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40562 | 40562 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
40563 | 40563 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
40564 | 40565 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
40566 | 40567 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
40568 | 40568 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40569 | 40569 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40570 | 40570 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
40571 | 40572 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
40573 | 40574 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
40575 | 40575 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40576 | 40576 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
40577 | 40577 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
40578 | 40579 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40580 | 40581 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40582 | 40582 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40583 | 40583 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40584 | 40584 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
40585 | 40586 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
40587 | 40588 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40589 | 40589 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
40590 | 40590 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
40591 | 40591 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
40592 | 40592 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
40593 | 40593 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40594 | 40594 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
40595 | 40595 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
40596 | 40596 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
40597 | 40597 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
40598 | 40598 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
40599 | 40599 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40600 | 40600 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40601 | 40601 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40602 | 40602 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40603 | 40603 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40604 | 40604 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
40605 | 40605 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40606 | 40606 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40607 | 40607 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
40608 | 40608 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
40609 | 40609 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40610 | 40610 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40611 | 40611 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40612 | 40612 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
40613 | 40613 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40614 | 40615 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40616 | 40617 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40618 | 40618 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40619 | 40619 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40620 | 40620 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
40621 | 40621 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
40622 | 40622 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
40623 | 40623 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40624 | 40624 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
40625 | 40625 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40626 | 40626 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40627 | 40627 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40628 | 40628 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40629 | 40630 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40631 | 40631 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40632 | 40632 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40633 | 40633 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40634 | 40634 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40635 | 40635 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40636 | 40636 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40637 | 40637 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40638 | 40638 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40639 | 40639 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40640 | 40640 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
40641 | 40641 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40642 | 40642 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
40643 | 40643 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40644 | 40644 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40645 | 40645 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40646 | 40646 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40647 | 40648 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40649 | 40649 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40650 | 40650 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40651 | 40651 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40652 | 40652 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40653 | 40653 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40654 | 40654 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40655 | 40655 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40656 | 40656 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40657 | 40657 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40658 | 40658 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
40659 | 40659 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40660 | 40660 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
40661 | 40661 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40662 | 40662 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40663 | 40663 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40664 | 40664 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40665 | 40666 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40667 | 40667 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40668 | 40668 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40669 | 40669 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40670 | 40670 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40671 | 40671 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40672 | 40672 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40673 | 40673 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40674 | 40674 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40675 | 40675 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40676 | 40676 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
40677 | 40677 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40678 | 40678 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
40679 | 40679 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40680 | 40680 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40681 | 40681 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40682 | 40682 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40683 | 40684 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40685 | 40685 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40686 | 40686 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40687 | 40687 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40688 | 40688 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40689 | 40689 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40690 | 40690 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40691 | 40691 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40692 | 40692 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40693 | 40693 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40694 | 40694 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
40695 | 40695 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
40696 | 40696 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40697 | 40697 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40698 | 40698 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40699 | 40699 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
40700 | 40700 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40701 | 40702 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40703 | 40704 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40705 | 40705 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40706 | 40706 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40707 | 40707 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
40708 | 40708 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
40709 | 40709 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40710 | 40710 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40711 | 40712 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40713 | 40713 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40714 | 40714 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40715 | 40715 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40716 | 40716 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40717 | 40717 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40718 | 40718 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40719 | 40719 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40720 | 40720 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40721 | 40721 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40722 | 40723 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40724 | 40724 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40725 | 40725 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40726 | 40726 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40727 | 40727 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40728 | 40728 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40729 | 40729 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40730 | 40730 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40731 | 40731 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40732 | 40732 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40733 | 40734 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40735 | 40735 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40736 | 40736 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40737 | 40737 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40738 | 40738 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40739 | 40739 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40740 | 40740 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40741 | 40741 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40742 | 40742 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40743 | 40743 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40744 | 40745 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40746 | 40746 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40747 | 40747 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40748 | 40748 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40749 | 40749 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40750 | 40750 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40751 | 40751 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40752 | 40752 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40753 | 40753 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
40754 | 40754 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
40755 | 40755 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40756 | 40756 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40757 | 40757 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40758 | 40758 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40759 | 40759 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40760 | 40760 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40761 | 40761 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40762 | 40762 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40763 | 40763 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40764 | 40764 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40765 | 40766 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40767 | 40767 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40768 | 40769 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40770 | 40770 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40771 | 40772 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40773 | 40773 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40774 | 40775 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40776 | 40776 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40777 | 40778 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40779 | 40779 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40780 | 40780 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40781 | 40782 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40783 | 40783 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40784 | 40785 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40786 | 40786 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40787 | 40788 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40789 | 40789 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40790 | 40791 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40792 | 40792 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40793 | 40794 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40795 | 40795 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40796 | 40796 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40797 | 40798 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40799 | 40799 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40800 | 40801 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40802 | 40802 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40803 | 40804 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40805 | 40805 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40806 | 40807 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40808 | 40808 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40809 | 40810 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40811 | 40811 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40812 | 40812 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40813 | 40813 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40814 | 40815 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40816 | 40816 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40817 | 40818 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40819 | 40819 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40820 | 40821 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40822 | 40822 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40823 | 40824 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40825 | 40825 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40826 | 40827 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40828 | 40828 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40829 | 40829 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40830 | 40831 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40832 | 40832 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40833 | 40834 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40835 | 40835 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40836 | 40837 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40838 | 40838 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40839 | 40840 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40841 | 40841 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40842 | 40843 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40844 | 40844 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40845 | 40845 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40846 | 40847 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40848 | 40848 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40849 | 40850 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40851 | 40851 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40852 | 40853 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40854 | 40854 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40855 | 40856 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40857 | 40857 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40858 | 40859 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40860 | 40860 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40861 | 40861 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40862 | 40862 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40863 | 40864 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40865 | 40865 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40866 | 40867 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40868 | 40868 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40869 | 40870 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40871 | 40871 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40872 | 40873 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40874 | 40874 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40875 | 40876 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40877 | 40877 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40878 | 40878 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40879 | 40880 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40881 | 40881 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40882 | 40883 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40884 | 40884 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40885 | 40886 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40887 | 40887 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40888 | 40889 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40890 | 40890 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40891 | 40892 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40893 | 40893 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40894 | 40894 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40895 | 40896 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40897 | 40897 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40898 | 40899 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40900 | 40900 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40901 | 40902 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40903 | 40903 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40904 | 40905 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40906 | 40906 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40907 | 40908 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40909 | 40909 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40910 | 40910 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40911 | 40911 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40912 | 40913 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40914 | 40914 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40915 | 40916 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40917 | 40917 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40918 | 40919 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40920 | 40920 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40921 | 40922 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40923 | 40923 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40924 | 40925 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40926 | 40926 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40927 | 40927 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40928 | 40929 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40930 | 40930 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40931 | 40932 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40933 | 40933 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40934 | 40935 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40936 | 40936 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40937 | 40938 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40939 | 40939 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40940 | 40941 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40942 | 40942 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40943 | 40943 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40944 | 40945 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40946 | 40946 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40947 | 40948 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40949 | 40949 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40950 | 40951 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40952 | 40952 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40953 | 40954 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40955 | 40955 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40956 | 40957 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40958 | 40958 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
40959 | 40959 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
40960 | 40960 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40961 | 40961 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40962 | 40962 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40963 | 40963 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40964 | 40964 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40965 | 40965 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40966 | 40966 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40967 | 40967 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40968 | 40968 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40969 | 40969 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40970 | 40971 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40972 | 40972 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40973 | 40974 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40975 | 40975 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40976 | 40977 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40978 | 40978 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40979 | 40980 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40981 | 40981 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40982 | 40983 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40984 | 40984 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40985 | 40985 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40986 | 40987 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40988 | 40988 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40989 | 40990 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40991 | 40991 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40992 | 40993 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40994 | 40994 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40995 | 40996 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40997 | 40997 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40998 | 40999 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41000 | 41000 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41001 | 41001 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41002 | 41003 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41004 | 41004 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41005 | 41006 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41007 | 41007 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41008 | 41009 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41010 | 41010 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41011 | 41012 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41013 | 41013 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41014 | 41015 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41016 | 41016 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41017 | 41017 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41018 | 41018 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41019 | 41020 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41021 | 41021 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41022 | 41023 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41024 | 41024 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41025 | 41026 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41027 | 41027 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41028 | 41029 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41030 | 41030 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41031 | 41032 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41033 | 41033 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41034 | 41034 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41035 | 41036 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41037 | 41037 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41038 | 41039 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41040 | 41040 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41041 | 41042 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41043 | 41043 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41044 | 41045 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41046 | 41046 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41047 | 41048 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41049 | 41049 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41050 | 41050 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41051 | 41052 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41053 | 41053 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41054 | 41055 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41056 | 41056 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41057 | 41058 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41059 | 41059 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41060 | 41061 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41062 | 41062 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41063 | 41064 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41065 | 41065 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41066 | 41066 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41067 | 41067 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41068 | 41069 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41070 | 41070 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41071 | 41072 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41073 | 41073 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41074 | 41075 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41076 | 41076 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41077 | 41078 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41079 | 41079 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41080 | 41081 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41082 | 41082 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41083 | 41083 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41084 | 41085 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41086 | 41086 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41087 | 41088 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41089 | 41089 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41090 | 41091 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41092 | 41092 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41093 | 41094 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41095 | 41095 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41096 | 41097 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41098 | 41098 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41099 | 41099 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41100 | 41101 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41102 | 41102 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41103 | 41104 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41105 | 41105 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41106 | 41107 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41108 | 41108 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41109 | 41110 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41111 | 41111 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41112 | 41113 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41114 | 41114 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41115 | 41115 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41116 | 41116 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41117 | 41118 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41119 | 41119 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41120 | 41121 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41122 | 41122 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41123 | 41124 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41125 | 41125 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41126 | 41127 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41128 | 41128 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41129 | 41130 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41131 | 41131 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41132 | 41132 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41133 | 41134 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41135 | 41135 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41136 | 41137 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41138 | 41138 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41139 | 41140 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41141 | 41141 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41142 | 41143 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41144 | 41144 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41145 | 41146 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41147 | 41147 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41148 | 41148 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41149 | 41150 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41151 | 41151 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41152 | 41153 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41154 | 41154 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41155 | 41156 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41157 | 41157 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41158 | 41159 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41160 | 41160 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41161 | 41162 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41163 | 41163 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
41164 | 41164 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
41165 | 41165 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41166 | 41166 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41167 | 41167 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41168 | 41168 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41169 | 41169 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41170 | 41170 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41171 | 41171 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41172 | 41172 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41173 | 41173 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41174 | 41175 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41176 | 41177 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41178 | 41179 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41180 | 41181 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41182 | 41183 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41184 | 41185 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41186 | 41187 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41188 | 41189 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41190 | 41191 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41192 | 41193 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41194 | 41194 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41195 | 41196 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41197 | 41198 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41199 | 41200 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41201 | 41202 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41203 | 41204 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41205 | 41206 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41207 | 41208 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41209 | 41210 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41211 | 41212 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41213 | 41214 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41215 | 41215 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41216 | 41217 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41218 | 41219 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41220 | 41221 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41222 | 41223 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41224 | 41225 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41226 | 41227 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41228 | 41229 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41230 | 41231 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41232 | 41233 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41234 | 41235 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41236 | 41236 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41237 | 41237 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41238 | 41239 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41240 | 41241 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41242 | 41243 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41244 | 41245 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41246 | 41247 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41248 | 41249 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41250 | 41251 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41252 | 41253 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41254 | 41255 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41256 | 41257 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41258 | 41258 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41259 | 41260 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41261 | 41262 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41263 | 41264 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41265 | 41266 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41267 | 41268 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41269 | 41270 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41271 | 41272 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41273 | 41274 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41275 | 41276 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41277 | 41278 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41279 | 41279 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41280 | 41281 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41282 | 41283 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41284 | 41285 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41286 | 41287 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41288 | 41289 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41290 | 41291 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41292 | 41293 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41294 | 41295 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41296 | 41297 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41298 | 41299 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41300 | 41300 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41301 | 41301 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41302 | 41303 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41304 | 41305 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41306 | 41307 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41308 | 41309 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41310 | 41311 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41312 | 41313 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41314 | 41315 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41316 | 41317 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41318 | 41319 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41320 | 41321 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41322 | 41322 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41323 | 41324 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41325 | 41326 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41327 | 41328 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41329 | 41330 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41331 | 41332 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41333 | 41334 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41335 | 41336 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41337 | 41338 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41339 | 41340 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41341 | 41342 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41343 | 41343 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41344 | 41345 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41346 | 41347 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41348 | 41349 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41350 | 41351 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41352 | 41353 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41354 | 41355 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41356 | 41357 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41358 | 41359 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41360 | 41361 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41362 | 41363 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41364 | 41364 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41365 | 41365 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41366 | 41367 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41368 | 41369 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41370 | 41371 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41372 | 41373 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41374 | 41375 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41376 | 41377 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41378 | 41379 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41380 | 41381 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41382 | 41383 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41384 | 41385 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41386 | 41386 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41387 | 41388 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41389 | 41390 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41391 | 41392 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41393 | 41394 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41395 | 41396 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41397 | 41398 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41399 | 41400 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41401 | 41402 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41403 | 41404 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41405 | 41406 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41407 | 41407 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41408 | 41409 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41410 | 41411 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41412 | 41413 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41414 | 41415 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41416 | 41417 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41418 | 41419 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41420 | 41421 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41422 | 41423 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41424 | 41425 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41426 | 41427 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41428 | 41428 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
41429 | 41429 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
41430 | 41430 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41431 | 41431 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41432 | 41432 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41433 | 41433 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41434 | 41434 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41435 | 41435 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41436 | 41436 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41437 | 41437 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41438 | 41438 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41439 | 41440 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41441 | 41442 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41443 | 41444 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41445 | 41446 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41447 | 41448 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41449 | 41450 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41451 | 41452 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41453 | 41454 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41455 | 41456 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41457 | 41458 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41459 | 41459 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41460 | 41461 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41462 | 41463 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41464 | 41465 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41466 | 41467 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41468 | 41469 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41470 | 41471 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41472 | 41473 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41474 | 41475 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41476 | 41477 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41478 | 41479 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41480 | 41480 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41481 | 41482 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41483 | 41484 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41485 | 41486 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41487 | 41488 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41489 | 41490 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41491 | 41492 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41493 | 41494 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41495 | 41496 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41497 | 41498 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41499 | 41500 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41501 | 41501 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41502 | 41502 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41503 | 41504 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41505 | 41506 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41507 | 41508 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41509 | 41510 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41511 | 41512 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41513 | 41514 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41515 | 41516 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41517 | 41518 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41519 | 41520 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41521 | 41522 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41523 | 41523 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41524 | 41525 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41526 | 41527 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41528 | 41529 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41530 | 41531 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41532 | 41533 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41534 | 41535 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41536 | 41537 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41538 | 41539 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41540 | 41541 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41542 | 41543 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41544 | 41544 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41545 | 41546 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41547 | 41548 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41549 | 41550 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41551 | 41552 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41553 | 41554 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41555 | 41556 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41557 | 41558 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41559 | 41560 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41561 | 41562 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41563 | 41564 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41565 | 41565 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41566 | 41566 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41567 | 41568 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41569 | 41570 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41571 | 41572 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41573 | 41574 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41575 | 41576 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41577 | 41578 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41579 | 41580 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41581 | 41582 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41583 | 41584 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41585 | 41586 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41587 | 41587 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41588 | 41589 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41590 | 41591 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41592 | 41593 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41594 | 41595 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41596 | 41597 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41598 | 41599 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41600 | 41601 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41602 | 41603 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41604 | 41605 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41606 | 41607 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41608 | 41608 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41609 | 41610 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41611 | 41612 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41613 | 41614 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41615 | 41616 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41617 | 41618 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41619 | 41620 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41621 | 41622 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41623 | 41624 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41625 | 41626 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41627 | 41628 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41629 | 41629 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41630 | 41630 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41631 | 41632 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41633 | 41634 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41635 | 41636 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41637 | 41638 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41639 | 41640 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41641 | 41642 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41643 | 41644 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41645 | 41646 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41647 | 41648 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41649 | 41650 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41651 | 41651 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41652 | 41653 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41654 | 41655 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41656 | 41657 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41658 | 41659 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41660 | 41661 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41662 | 41663 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41664 | 41665 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41666 | 41667 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41668 | 41669 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41670 | 41671 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41672 | 41672 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41673 | 41674 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41675 | 41676 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41677 | 41678 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41679 | 41680 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41681 | 41682 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41683 | 41684 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41685 | 41686 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41687 | 41688 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41689 | 41690 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41691 | 41692 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41693 | 41693 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
41694 | 41694 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
41695 | 41695 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41696 | 41696 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
41697 | 41697 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41698 | 41698 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
41699 | 41700 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41701 | 41702 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41703 | 41703 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
41704 | 41704 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
41705 | 41705 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
41706 | 41706 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
41707 | 41708 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41709 | 41710 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41711 | 41711 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41712 | 41712 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41713 | 41714 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41715 | 41715 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41716 | 41716 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
41717 | 41718 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41719 | 41720 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41721 | 41721 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41722 | 41722 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41723 | 41724 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41725 | 41725 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41726 | 41726 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41727 | 41728 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41729 | 41730 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41731 | 41731 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41732 | 41732 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41733 | 41734 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41735 | 41735 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41736 | 41736 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41737 | 41738 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41739 | 41740 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41741 | 41741 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41742 | 41742 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41743 | 41744 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41745 | 41745 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41746 | 41746 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41747 | 41747 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
41748 | 41748 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
41749 | 41749 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41750 | 41750 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
41751 | 41751 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41752 | 41752 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
41753 | 41753 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
41754 | 41755 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41756 | 41757 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41758 | 41758 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
41759 | 41759 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
41760 | 41760 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
41761 | 41761 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
41762 | 41762 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41763 | 41763 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
41764 | 41764 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41765 | 41765 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41766 | 41766 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41767 | 41767 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41768 | 41768 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41769 | 41769 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41770 | 41770 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41771 | 41771 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41772 | 41772 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41773 | 41773 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41774 | 41774 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41775 | 41775 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41776 | 41776 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41777 | 41777 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
41778 | 41778 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41779 | 41779 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
41780 | 41780 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41781 | 41781 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41782 | 41782 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41783 | 41783 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41784 | 41784 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41785 | 41785 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41786 | 41786 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41787 | 41787 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41788 | 41788 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41789 | 41789 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41790 | 41790 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41791 | 41791 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41792 | 41792 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41793 | 41793 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
41794 | 41794 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41795 | 41795 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
41796 | 41796 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41797 | 41797 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41798 | 41798 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41799 | 41799 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41800 | 41800 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41801 | 41801 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41802 | 41802 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41803 | 41803 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41804 | 41804 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41805 | 41805 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41806 | 41806 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41807 | 41807 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41808 | 41808 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41809 | 41809 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
41810 | 41810 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41811 | 41811 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
41812 | 41812 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41813 | 41813 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41814 | 41814 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41815 | 41815 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41816 | 41816 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41817 | 41817 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41818 | 41818 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41819 | 41819 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41820 | 41820 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41821 | 41821 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41822 | 41822 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41823 | 41823 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41824 | 41824 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41825 | 41825 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
41826 | 41826 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
41827 | 41827 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
41828 | 41828 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
41829 | 41829 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
41830 | 41830 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
41831 | 41831 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
41832 | 41832 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
41833 | 41833 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41834 | 41834 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
41835 | 41835 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Primo GEN24 6.0 Primo GEN24 10.0 Primo GEN24 10.0 208-240 Primo GEN24 3.0 Primo GEN24 3.6 Primo GEN24 3.8 208-240 Primo GEN24 4.0 Primo GEN24 4.6 Primo GEN24 5.0 Primo GEN24 6.0 208-240 Symo GEN24 10.0 Symo GEN24 3.0 Symo GEN24 4.0 Symo GEN24 5.0 Symo GEN24 6.0 Symo GEN24 8.0
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (11x)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (11x) | uint16 |  |  | 111, 113
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (11x) | uint16 | Registers |  | 60
3 | 4 | 2 | R | 0x03 | A | AC Current | float32 | A
5 | 6 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
7 | 8 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
9 | 10 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
11 | 12 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
13 | 14 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
15 | 16 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
17 | 18 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
19 | 20 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
21 | 22 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
23 | 24 | 2 | R | 0x03 | W | AC Power | float32 | W
25 | 26 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
27 | 28 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
29 | 30 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
31 | 32 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
33 | 34 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
35 | 36 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
37 | 38 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
39 | 40 | 2 | R | 0x03 | DCW | DC Power | float32 | W
41 | 42 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
43 | 44 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
45 | 46 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
47 | 48 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
49 | 49 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
50 | 50 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
51 | 52 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
53 | 54 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
55 | 56 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
57 | 58 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
59 | 60 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
61 | 62 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 48
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 2 MPPT => 2 repeating blocks
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
31 | 31 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40 | 40 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
41 | 41 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
42 | 42 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
43 | 44 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
45 | 46 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
47 | 47 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
48 | 48 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
49 | 50 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported

## DERMeasureAC (701)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
3 | 3 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
4 | 4 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
5 | 5 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
6 | 6 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
7 | 8 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
9 | 10 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
11 | 11 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
12 | 12 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
13 | 13 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
14 | 14 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
15 | 15 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
16 | 16 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
17 | 17 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
18 | 19 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
20 | 23 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
24 | 27 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
28 | 31 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
32 | 35 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
39 | 39 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40 | 40 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
41 | 41 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
42 | 42 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
43 | 43 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
44 | 44 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
45 | 45 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
46 | 46 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
47 | 47 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
48 | 48 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
49 | 52 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
53 | 56 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
57 | 60 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
61 | 64 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
65 | 65 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
66 | 66 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
67 | 67 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
68 | 68 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
69 | 69 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
70 | 70 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
71 | 71 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
72 | 75 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
76 | 79 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
80 | 83 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
84 | 87 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
88 | 88 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
89 | 89 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
90 | 90 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
91 | 91 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
92 | 92 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
93 | 93 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
94 | 94 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
95 | 98 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
99 | 102 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
103 | 106 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
107 | 110 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
111 | 111 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
112 | 113 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
114 | 114 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
115 | 115 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
116 | 116 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
117 | 117 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
118 | 118 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
119 | 119 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
120 | 120 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
121 | 121 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
122 | 122 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
123 | 123 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
124 | 155 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported

## DERCapacity (702)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
4 | 4 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
5 | 5 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
6 | 6 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
7 | 7 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
8 | 8 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
9 | 9 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
10 | 10 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
11 | 11 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
12 | 12 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
13 | 13 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
14 | 14 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
15 | 15 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
16 | 16 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
17 | 17 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
19 | 19 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
20 | 20 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
21 | 21 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
22 | 22 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
23 | 23 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
24 | 25 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
26 | 26 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
27 | 27 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
28 | 28 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
29 | 29 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
30 | 30 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
31 | 31 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
32 | 32 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
33 | 33 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
34 | 34 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
35 | 35 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
36 | 36 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
37 | 37 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
38 | 38 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
39 | 39 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40 | 40 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
41 | 41 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
42 | 42 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
43 | 43 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
44 | 44 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
45 | 45 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
46 | 46 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
47 | 47 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
48 | 48 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
49 | 49 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
50 | 50 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
51 | 51 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
52 | 52 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6

## DEREnterService (703)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
3 | 3 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
5 | 5 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
6 | 7 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
8 | 9 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
10 | 11 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
12 | 13 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
14 | 15 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
18 | 18 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2

## DERCtlAC (704)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
3 | 3 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
5 | 6 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
7 | 8 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
9 | 9 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
10 | 10 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
11 | 12 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
13 | 14 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
15 | 15 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
17 | 17 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
18 | 18 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
19 | 20 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
21 | 22 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
23 | 23 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
24 | 24 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
25 | 26 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
27 | 28 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
29 | 29 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
30 | 30 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
31 | 31 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
32 | 33 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
34 | 35 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
36 | 36 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
37 | 37 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
38 | 38 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
39 | 40 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
41 | 42 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
43 | 43 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
46 | 47 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
48 | 49 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
50 | 50 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
51 | 51 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
52 | 52 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
53 | 53 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
54 | 54 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
55 | 55 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
56 | 56 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
57 | 57 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
58 | 58 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
59 | 59 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
60 | 60 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
62 | 62 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
64 | 64 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
65 | 65 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
66 | 66 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
67 | 67 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported

## DERVoltVar (705)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
23 | 24 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
59 | 60 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
66 | 66 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
77 | 78 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
79 | 79 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
80 | 80 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
81 | 81 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
82 | 82 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
83 | 83 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
84 | 84 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
85 | 85 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
86 | 86 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
87 | 87 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERVoltWatt (706)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
29 | 30 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40 | 41 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%

## DERTripLV (707)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHV (708)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripLF (709)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHF (710)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERFreqDroop (711)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
7 | 8 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
9 | 10 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
11 | 11 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
12 | 12 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
13 | 13 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
14 | 14 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
15 | 16 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
17 | 18 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
21 | 22 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
24 | 24 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
27 | 28 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
31 | 32 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
34 | 34 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
35 | 36 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
37 | 38 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
44 | 44 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
45 | 46 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
47 | 48 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
54 | 54 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)

## DERWattVar (712)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
18 | 18 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
34 | 34 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41 | 41 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
50 | 50 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
66 | 66 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
77 | 77 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
78 | 78 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERStorageCapacity (713)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
3 | 3 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
4 | 4 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
5 | 5 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
6 | 6 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
7 | 7 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
8 | 8 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
9 | 9 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0