## Complete Map
Fronius Tauro ECO Inverter Register Map with Integer+SF Inverter Model for US use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Tauro ECO 50-3-P Tauro ECO 50-3-P Tauro ECO 99-3-D Tauro ECO 100-3-P Tauro ECO 100-3-D
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (103) | uint16 |  |  | 103
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (103) | uint16 | Registers |  | 50
40072 | 40072 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF
40075 | 40075 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF
40076 | 40076 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
40077 | 40077 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF
40078 | 40078 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF
40079 | 40079 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF
40080 | 40080 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
40081 | 40081 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF
40082 | 40082 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF
40083 | 40083 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
40084 | 40084 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
40085 | 40085 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
40086 | 40086 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
40088 | 40088 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
40089 | 40089 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
40090 | 40090 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
40091 | 40091 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
40092 | 40092 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
40093 | 40093 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
40094 | 40095 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
40096 | 40096 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
40097 | 40097 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF
40098 | 40098 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | auto-scaled on DCA
40099 | 40099 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF
40100 | 40100 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | auto-scaled on DCV
40101 | 40101 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
40102 | 40102 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
40103 | 40103 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
40104 | 40104 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
40105 | 40105 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
40106 | 40106 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
40107 | 40107 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
40108 | 40108 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40109 | 40109 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40110 | 40111 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40112 | 40113 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40114 | 40115 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40116 | 40117 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40118 | 40119 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40120 | 40121 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40122 | 40122 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40123 | 40123 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40124 | 40124 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
40125 | 40125 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40126 | 40126 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40127 | 40127 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40128 | 40128 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40129 | 40129 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40130 | 40130 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
40131 | 40131 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
40132 | 40132 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40133 | 40133 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40134 | 40134 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40135 | 40135 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40136 | 40136 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40137 | 40137 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
40138 | 40138 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
40139 | 40139 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40140 | 40140 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40141 | 40141 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
40142 | 40142 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
40143 | 40143 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40144 | 40144 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40145 | 40145 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
40146 | 40146 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
40147 | 40147 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
40148 | 40148 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
40149 | 40149 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40150 | 40150 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40151 | 40151 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40152 | 40152 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40153 | 40153 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40154 | 40154 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40155 | 40155 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40156 | 40156 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40157 | 40157 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40158 | 40158 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40159 | 40159 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40160 | 40160 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40161 | 40161 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40162 | 40162 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40163 | 40163 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40164 | 40164 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40165 | 40165 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40166 | 40166 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40167 | 40167 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40168 | 40168 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40169 | 40169 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40170 | 40170 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40171 | 40171 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40172 | 40172 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40173 | 40173 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40174 | 40174 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40175 | 40175 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40176 | 40176 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40177 | 40177 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40178 | 40178 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40180 | 40180 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40181 | 40181 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40182 | 40182 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40183 | 40183 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40184 | 40184 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40185 | 40185 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40186 | 40186 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40187 | 40190 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40191 | 40194 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40195 | 40198 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40199 | 40202 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40203 | 40206 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40207 | 40210 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40211 | 40211 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40212 | 40212 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40213 | 40213 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40214 | 40214 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40215 | 40216 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40217 | 40218 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40219 | 40222 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40223 | 40224 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40225 | 40225 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40226 | 40226 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40227 | 40227 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40228 | 40228 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40229 | 40229 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40230 | 40230 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40231 | 40231 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40232 | 40232 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40233 | 40233 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40234 | 40234 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40235 | 40235 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40236 | 40236 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40237 | 40237 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40238 | 40238 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40239 | 40239 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40243 | 40243 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40245 | 40245 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40249 | 40249 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40251 | 40251 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40252 | 40252 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40253 | 40253 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40254 | 40254 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40255 | 40255 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 28
40256 | 40256 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40257 | 40257 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40258 | 40258 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40259 | 40259 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40260 | 40261 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40262 | 40262 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 1 MPPT => 1 repeating block
40263 | 40263 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40264 | 40264 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40265 | 40272 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40273 | 40273 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40274 | 40274 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40275 | 40275 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40276 | 40277 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40278 | 40279 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40280 | 40280 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40281 | 40281 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40282 | 40283 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40284 | 40284 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
40285 | 40285 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
40286 | 40286 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
40287 | 40287 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
40288 | 40288 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
40289 | 40289 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
40290 | 40291 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
40292 | 40293 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
40294 | 40294 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
40295 | 40295 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
40296 | 40296 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
40297 | 40297 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
40298 | 40298 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
40299 | 40299 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
40300 | 40300 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
40301 | 40302 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
40303 | 40306 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
40307 | 40310 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
40311 | 40314 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
40315 | 40318 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
40319 | 40319 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
40320 | 40320 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
40321 | 40321 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
40322 | 40322 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40323 | 40323 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
40324 | 40324 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
40325 | 40325 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
40326 | 40326 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
40327 | 40327 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
40328 | 40328 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
40329 | 40329 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
40330 | 40330 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
40331 | 40331 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
40332 | 40335 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
40336 | 40339 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
40340 | 40343 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
40344 | 40347 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
40348 | 40348 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
40349 | 40349 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
40350 | 40350 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
40351 | 40351 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
40352 | 40352 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
40353 | 40353 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
40354 | 40354 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
40355 | 40358 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
40359 | 40362 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
40363 | 40366 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
40367 | 40370 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
40371 | 40371 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
40372 | 40372 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
40373 | 40373 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
40374 | 40374 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
40375 | 40375 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
40376 | 40376 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
40377 | 40377 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
40378 | 40381 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
40382 | 40385 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
40386 | 40389 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
40390 | 40393 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
40394 | 40394 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
40395 | 40396 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
40397 | 40397 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40398 | 40398 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40399 | 40399 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
40400 | 40400 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40401 | 40401 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
40402 | 40402 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
40403 | 40403 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40404 | 40404 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
40405 | 40405 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
40406 | 40406 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
40407 | 40438 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40439 | 40439 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
40440 | 40440 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
40441 | 40441 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
40442 | 40442 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
40443 | 40443 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40444 | 40444 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
40445 | 40445 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40446 | 40446 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
40447 | 40447 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
40448 | 40448 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
40449 | 40449 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40450 | 40450 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40451 | 40451 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
40452 | 40452 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
40453 | 40453 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
40454 | 40454 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
40455 | 40455 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
40456 | 40456 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
40457 | 40457 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
40458 | 40458 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
40459 | 40459 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
40460 | 40460 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
40461 | 40461 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
40462 | 40463 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
40464 | 40464 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
40465 | 40465 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
40466 | 40466 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
40467 | 40467 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
40468 | 40468 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
40469 | 40469 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
40470 | 40470 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
40471 | 40471 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
40472 | 40472 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
40473 | 40473 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
40474 | 40474 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
40475 | 40475 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
40476 | 40476 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
40477 | 40477 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40478 | 40478 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
40479 | 40479 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
40480 | 40480 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
40481 | 40481 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
40482 | 40482 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
40483 | 40483 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
40484 | 40484 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40485 | 40485 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40486 | 40486 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
40487 | 40487 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40488 | 40488 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40489 | 40489 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40490 | 40490 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40491 | 40491 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
40492 | 40492 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
40493 | 40493 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
40494 | 40494 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
40495 | 40495 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40496 | 40497 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40498 | 40499 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40500 | 40501 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
40502 | 40503 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
40504 | 40505 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
40506 | 40507 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
40508 | 40508 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
40509 | 40509 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40510 | 40510 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
40511 | 40511 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
40512 | 40512 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
40513 | 40513 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40514 | 40515 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40516 | 40517 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40518 | 40518 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
40519 | 40519 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
40520 | 40521 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
40522 | 40523 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
40524 | 40524 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
40525 | 40525 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40526 | 40526 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40527 | 40527 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
40528 | 40529 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
40530 | 40531 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40532 | 40532 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
40533 | 40533 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
40534 | 40535 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
40536 | 40537 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
40538 | 40538 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40539 | 40539 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40540 | 40540 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
40541 | 40542 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
40543 | 40544 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
40545 | 40545 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40546 | 40546 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
40547 | 40547 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
40548 | 40549 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40550 | 40551 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40552 | 40552 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40553 | 40553 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40554 | 40554 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
40555 | 40556 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
40557 | 40558 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40559 | 40559 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
40560 | 40560 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
40561 | 40561 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
40562 | 40562 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
40563 | 40563 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40564 | 40564 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
40565 | 40565 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
40566 | 40566 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
40567 | 40567 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
40568 | 40568 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
40569 | 40569 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40570 | 40570 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40571 | 40571 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40572 | 40572 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40573 | 40573 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40574 | 40574 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
40575 | 40575 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40576 | 40576 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40577 | 40577 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
40578 | 40578 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
40579 | 40579 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40580 | 40580 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40581 | 40581 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40582 | 40582 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
40583 | 40583 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40584 | 40585 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40586 | 40587 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40588 | 40588 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40589 | 40589 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40590 | 40590 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
40591 | 40591 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
40592 | 40592 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
40593 | 40593 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40594 | 40594 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
40595 | 40595 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40596 | 40596 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40597 | 40597 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40598 | 40598 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40599 | 40600 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40601 | 40601 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40602 | 40602 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40603 | 40603 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40604 | 40604 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40605 | 40605 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40606 | 40606 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40607 | 40607 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40608 | 40608 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40609 | 40609 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40610 | 40610 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
40611 | 40611 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40612 | 40612 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
40613 | 40613 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40614 | 40614 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40615 | 40615 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40616 | 40616 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40617 | 40618 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40619 | 40619 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40620 | 40620 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40621 | 40621 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40622 | 40622 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40623 | 40623 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40624 | 40624 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40625 | 40625 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40626 | 40626 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40627 | 40627 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40628 | 40628 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
40629 | 40629 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40630 | 40630 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
40631 | 40631 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40632 | 40632 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40633 | 40633 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40634 | 40634 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40635 | 40636 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40637 | 40637 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40638 | 40638 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40639 | 40639 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40640 | 40640 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40641 | 40641 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40642 | 40642 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40643 | 40643 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40644 | 40644 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40645 | 40645 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40646 | 40646 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
40647 | 40647 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40648 | 40648 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
40649 | 40649 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40650 | 40650 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40651 | 40651 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40652 | 40652 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40653 | 40654 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40655 | 40655 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40656 | 40656 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40657 | 40657 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40658 | 40658 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40659 | 40659 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40660 | 40660 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40661 | 40661 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40662 | 40662 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40663 | 40663 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40664 | 40664 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
40665 | 40665 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
40666 | 40666 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40667 | 40667 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40668 | 40668 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40669 | 40669 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
40670 | 40670 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40671 | 40672 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40673 | 40674 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40675 | 40675 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40676 | 40676 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40677 | 40677 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
40678 | 40678 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
40679 | 40679 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40680 | 40680 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40681 | 40682 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40683 | 40683 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40684 | 40684 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40685 | 40685 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40686 | 40686 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40687 | 40687 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40688 | 40688 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40689 | 40689 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40690 | 40690 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40691 | 40691 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40692 | 40693 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40694 | 40694 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40695 | 40695 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40696 | 40696 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40697 | 40697 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40698 | 40698 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40699 | 40699 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40700 | 40700 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40701 | 40701 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40702 | 40702 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40703 | 40704 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40705 | 40705 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40706 | 40706 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40707 | 40707 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40708 | 40708 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40709 | 40709 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40710 | 40710 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40711 | 40711 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40712 | 40712 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40713 | 40713 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40714 | 40715 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40716 | 40716 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40717 | 40717 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40718 | 40718 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40719 | 40719 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40720 | 40720 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40721 | 40721 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40722 | 40722 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40723 | 40723 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
40724 | 40724 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
40725 | 40725 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40726 | 40726 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40727 | 40727 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40728 | 40728 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40729 | 40729 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40730 | 40730 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40731 | 40731 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40732 | 40732 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40733 | 40733 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40734 | 40734 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40735 | 40736 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40737 | 40737 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40738 | 40739 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40740 | 40740 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40741 | 40742 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40743 | 40743 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40744 | 40745 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40746 | 40746 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40747 | 40748 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40749 | 40749 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40750 | 40750 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40751 | 40752 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40753 | 40753 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40754 | 40755 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40756 | 40756 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40757 | 40758 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40759 | 40759 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40760 | 40761 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40762 | 40762 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40763 | 40764 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40765 | 40765 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40766 | 40766 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40767 | 40768 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40769 | 40769 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40770 | 40771 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40772 | 40772 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40773 | 40774 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40775 | 40775 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40776 | 40777 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40778 | 40778 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40779 | 40780 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40781 | 40781 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40782 | 40782 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40783 | 40783 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40784 | 40785 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40786 | 40786 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40787 | 40788 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40789 | 40789 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40790 | 40791 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40792 | 40792 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40793 | 40794 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40795 | 40795 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40796 | 40797 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40798 | 40798 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40799 | 40799 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40800 | 40801 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40802 | 40802 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40803 | 40804 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40805 | 40805 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40806 | 40807 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40808 | 40808 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40809 | 40810 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40811 | 40811 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40812 | 40813 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40814 | 40814 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40815 | 40815 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40816 | 40817 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40818 | 40818 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40819 | 40820 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40821 | 40821 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40822 | 40823 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40824 | 40824 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40825 | 40826 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40827 | 40827 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40828 | 40829 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40830 | 40830 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40831 | 40831 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40832 | 40832 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40833 | 40834 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40835 | 40835 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40836 | 40837 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40838 | 40838 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40839 | 40840 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40841 | 40841 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40842 | 40843 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40844 | 40844 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40845 | 40846 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40847 | 40847 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40848 | 40848 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40849 | 40850 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40851 | 40851 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40852 | 40853 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40854 | 40854 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40855 | 40856 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40857 | 40857 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40858 | 40859 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40860 | 40860 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40861 | 40862 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40863 | 40863 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40864 | 40864 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40865 | 40866 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40867 | 40867 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40868 | 40869 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40870 | 40870 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40871 | 40872 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40873 | 40873 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40874 | 40875 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40876 | 40876 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40877 | 40878 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40879 | 40879 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40880 | 40880 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40881 | 40881 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40882 | 40883 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40884 | 40884 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40885 | 40886 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40887 | 40887 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40888 | 40889 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40890 | 40890 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40891 | 40892 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40893 | 40893 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40894 | 40895 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40896 | 40896 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40897 | 40897 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40898 | 40899 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40900 | 40900 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40901 | 40902 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40903 | 40903 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40904 | 40905 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40906 | 40906 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40907 | 40908 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40909 | 40909 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40910 | 40911 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40912 | 40912 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40913 | 40913 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40914 | 40915 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40916 | 40916 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40917 | 40918 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40919 | 40919 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40920 | 40921 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40922 | 40922 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40923 | 40924 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40925 | 40925 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40926 | 40927 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40928 | 40928 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
40929 | 40929 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
40930 | 40930 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40931 | 40931 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40932 | 40932 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40933 | 40933 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40934 | 40934 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40935 | 40935 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40936 | 40936 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40937 | 40937 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40938 | 40938 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40939 | 40939 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40940 | 40941 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40942 | 40942 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40943 | 40944 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40945 | 40945 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40946 | 40947 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40948 | 40948 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40949 | 40950 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40951 | 40951 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40952 | 40953 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40954 | 40954 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40955 | 40955 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40956 | 40957 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40958 | 40958 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40959 | 40960 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40961 | 40961 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40962 | 40963 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40964 | 40964 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40965 | 40966 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40967 | 40967 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40968 | 40969 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40970 | 40970 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40971 | 40971 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40972 | 40973 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40974 | 40974 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40975 | 40976 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40977 | 40977 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40978 | 40979 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40980 | 40980 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40981 | 40982 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40983 | 40983 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40984 | 40985 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40986 | 40986 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40987 | 40987 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40988 | 40988 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40989 | 40990 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40991 | 40991 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40992 | 40993 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40994 | 40994 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40995 | 40996 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40997 | 40997 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40998 | 40999 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41000 | 41000 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41001 | 41002 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41003 | 41003 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41004 | 41004 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41005 | 41006 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41007 | 41007 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41008 | 41009 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41010 | 41010 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41011 | 41012 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41013 | 41013 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41014 | 41015 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41016 | 41016 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41017 | 41018 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41019 | 41019 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41020 | 41020 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41021 | 41022 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41023 | 41023 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41024 | 41025 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41026 | 41026 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41027 | 41028 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41029 | 41029 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41030 | 41031 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41032 | 41032 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41033 | 41034 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41035 | 41035 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41036 | 41036 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41037 | 41037 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41038 | 41039 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41040 | 41040 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41041 | 41042 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41043 | 41043 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41044 | 41045 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41046 | 41046 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41047 | 41048 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41049 | 41049 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41050 | 41051 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41052 | 41052 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41053 | 41053 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41054 | 41055 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41056 | 41056 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41057 | 41058 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41059 | 41059 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41060 | 41061 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41062 | 41062 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41063 | 41064 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41065 | 41065 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41066 | 41067 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41068 | 41068 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41069 | 41069 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41070 | 41071 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41072 | 41072 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41073 | 41074 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41075 | 41075 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41076 | 41077 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41078 | 41078 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41079 | 41080 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41081 | 41081 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41082 | 41083 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41084 | 41084 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41085 | 41085 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41086 | 41086 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41087 | 41088 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41089 | 41089 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41090 | 41091 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41092 | 41092 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41093 | 41094 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41095 | 41095 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41096 | 41097 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41098 | 41098 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41099 | 41100 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41101 | 41101 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41102 | 41102 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41103 | 41104 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41105 | 41105 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41106 | 41107 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41108 | 41108 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41109 | 41110 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41111 | 41111 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41112 | 41113 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41114 | 41114 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41115 | 41116 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41117 | 41117 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41118 | 41118 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41119 | 41120 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41121 | 41121 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41122 | 41123 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41124 | 41124 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41125 | 41126 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41127 | 41127 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41128 | 41129 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41130 | 41130 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41131 | 41132 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41133 | 41133 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
41134 | 41134 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
41135 | 41135 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41136 | 41136 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41137 | 41137 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41138 | 41138 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41139 | 41139 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41140 | 41140 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41141 | 41141 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41142 | 41142 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41143 | 41143 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41144 | 41145 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41146 | 41147 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41148 | 41149 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41150 | 41151 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41152 | 41153 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41154 | 41155 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41156 | 41157 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41158 | 41159 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41160 | 41161 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41162 | 41163 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41164 | 41164 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41165 | 41166 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41167 | 41168 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41169 | 41170 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41171 | 41172 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41173 | 41174 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41175 | 41176 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41177 | 41178 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41179 | 41180 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41181 | 41182 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41183 | 41184 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41185 | 41185 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41186 | 41187 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41188 | 41189 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41190 | 41191 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41192 | 41193 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41194 | 41195 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41196 | 41197 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41198 | 41199 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41200 | 41201 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41202 | 41203 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41204 | 41205 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41206 | 41206 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41207 | 41207 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41208 | 41209 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41210 | 41211 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41212 | 41213 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41214 | 41215 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41216 | 41217 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41218 | 41219 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41220 | 41221 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41222 | 41223 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41224 | 41225 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41226 | 41227 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41228 | 41228 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41229 | 41230 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41231 | 41232 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41233 | 41234 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41235 | 41236 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41237 | 41238 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41239 | 41240 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41241 | 41242 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41243 | 41244 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41245 | 41246 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41247 | 41248 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41249 | 41249 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41250 | 41251 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41252 | 41253 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41254 | 41255 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41256 | 41257 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41258 | 41259 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41260 | 41261 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41262 | 41263 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41264 | 41265 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41266 | 41267 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41268 | 41269 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41270 | 41270 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41271 | 41271 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41272 | 41273 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41274 | 41275 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41276 | 41277 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41278 | 41279 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41280 | 41281 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41282 | 41283 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41284 | 41285 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41286 | 41287 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41288 | 41289 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41290 | 41291 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41292 | 41292 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41293 | 41294 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41295 | 41296 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41297 | 41298 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41299 | 41300 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41301 | 41302 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41303 | 41304 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41305 | 41306 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41307 | 41308 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41309 | 41310 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41311 | 41312 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41313 | 41313 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41314 | 41315 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41316 | 41317 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41318 | 41319 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41320 | 41321 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41322 | 41323 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41324 | 41325 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41326 | 41327 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41328 | 41329 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41330 | 41331 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41332 | 41333 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41334 | 41334 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41335 | 41335 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41336 | 41337 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41338 | 41339 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41340 | 41341 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41342 | 41343 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41344 | 41345 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41346 | 41347 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41348 | 41349 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41350 | 41351 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41352 | 41353 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41354 | 41355 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41356 | 41356 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41357 | 41358 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41359 | 41360 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41361 | 41362 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41363 | 41364 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41365 | 41366 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41367 | 41368 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41369 | 41370 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41371 | 41372 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41373 | 41374 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41375 | 41376 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41377 | 41377 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41378 | 41379 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41380 | 41381 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41382 | 41383 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41384 | 41385 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41386 | 41387 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41388 | 41389 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41390 | 41391 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41392 | 41393 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41394 | 41395 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41396 | 41397 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41398 | 41398 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
41399 | 41399 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
41400 | 41400 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41401 | 41401 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41402 | 41402 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41403 | 41403 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41404 | 41404 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41405 | 41405 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41406 | 41406 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41407 | 41407 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41408 | 41408 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41409 | 41410 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41411 | 41412 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41413 | 41414 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41415 | 41416 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41417 | 41418 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41419 | 41420 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41421 | 41422 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41423 | 41424 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41425 | 41426 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41427 | 41428 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41429 | 41429 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41430 | 41431 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41432 | 41433 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41434 | 41435 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41436 | 41437 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41438 | 41439 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41440 | 41441 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41442 | 41443 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41444 | 41445 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41446 | 41447 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41448 | 41449 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41450 | 41450 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41451 | 41452 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41453 | 41454 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41455 | 41456 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41457 | 41458 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41459 | 41460 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41461 | 41462 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41463 | 41464 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41465 | 41466 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41467 | 41468 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41469 | 41470 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41471 | 41471 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41472 | 41472 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41473 | 41474 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41475 | 41476 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41477 | 41478 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41479 | 41480 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41481 | 41482 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41483 | 41484 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41485 | 41486 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41487 | 41488 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41489 | 41490 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41491 | 41492 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41493 | 41493 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41494 | 41495 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41496 | 41497 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41498 | 41499 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41500 | 41501 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41502 | 41503 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41504 | 41505 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41506 | 41507 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41508 | 41509 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41510 | 41511 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41512 | 41513 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41514 | 41514 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41515 | 41516 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41517 | 41518 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41519 | 41520 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41521 | 41522 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41523 | 41524 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41525 | 41526 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41527 | 41528 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41529 | 41530 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41531 | 41532 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41533 | 41534 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41535 | 41535 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41536 | 41536 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41537 | 41538 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41539 | 41540 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41541 | 41542 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41543 | 41544 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41545 | 41546 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41547 | 41548 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41549 | 41550 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41551 | 41552 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41553 | 41554 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41555 | 41556 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41557 | 41557 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41558 | 41559 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41560 | 41561 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41562 | 41563 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41564 | 41565 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41566 | 41567 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41568 | 41569 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41570 | 41571 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41572 | 41573 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41574 | 41575 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41576 | 41577 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41578 | 41578 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41579 | 41580 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41581 | 41582 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41583 | 41584 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41585 | 41586 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41587 | 41588 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41589 | 41590 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41591 | 41592 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41593 | 41594 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41595 | 41596 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41597 | 41598 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41599 | 41599 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41600 | 41600 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41601 | 41602 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41603 | 41604 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41605 | 41606 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41607 | 41608 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41609 | 41610 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41611 | 41612 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41613 | 41614 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41615 | 41616 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41617 | 41618 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41619 | 41620 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41621 | 41621 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41622 | 41623 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41624 | 41625 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41626 | 41627 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41628 | 41629 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41630 | 41631 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41632 | 41633 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41634 | 41635 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41636 | 41637 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41638 | 41639 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41640 | 41641 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41642 | 41642 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41643 | 41644 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41645 | 41646 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41647 | 41648 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41649 | 41650 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41651 | 41652 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41653 | 41654 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41655 | 41656 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41657 | 41658 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41659 | 41660 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41661 | 41662 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41663 | 41663 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
41664 | 41664 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
41665 | 41665 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41666 | 41666 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
41667 | 41667 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41668 | 41668 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
41669 | 41670 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41671 | 41672 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41673 | 41673 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
41674 | 41674 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
41675 | 41675 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
41676 | 41676 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
41677 | 41678 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41679 | 41680 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41681 | 41681 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41682 | 41682 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41683 | 41684 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41685 | 41685 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41686 | 41686 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
41687 | 41688 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41689 | 41690 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41691 | 41691 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41692 | 41692 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41693 | 41694 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41695 | 41695 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41696 | 41696 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41697 | 41698 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41699 | 41700 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41701 | 41701 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41702 | 41702 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41703 | 41704 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41705 | 41705 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41706 | 41706 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41707 | 41708 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41709 | 41710 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41711 | 41711 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41712 | 41712 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41713 | 41714 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41715 | 41715 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41716 | 41716 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41717 | 41717 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
41718 | 41718 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
41719 | 41719 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41720 | 41720 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
41721 | 41721 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41722 | 41722 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
41723 | 41723 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
41724 | 41725 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41726 | 41727 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41728 | 41728 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
41729 | 41729 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
41730 | 41730 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
41731 | 41731 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
41732 | 41732 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41733 | 41733 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
41734 | 41734 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41735 | 41735 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41736 | 41736 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41737 | 41737 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41738 | 41738 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41739 | 41739 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41740 | 41740 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41741 | 41741 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41742 | 41742 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41743 | 41743 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41744 | 41744 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41745 | 41745 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41746 | 41746 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41747 | 41747 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
41748 | 41748 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41749 | 41749 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
41750 | 41750 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41751 | 41751 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41752 | 41752 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41753 | 41753 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41754 | 41754 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41755 | 41755 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41756 | 41756 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41757 | 41757 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41758 | 41758 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41759 | 41759 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41760 | 41760 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41761 | 41761 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41762 | 41762 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41763 | 41763 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
41764 | 41764 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41765 | 41765 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
41766 | 41766 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41767 | 41767 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41768 | 41768 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41769 | 41769 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41770 | 41770 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41771 | 41771 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41772 | 41772 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41773 | 41773 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41774 | 41774 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41775 | 41775 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41776 | 41776 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41777 | 41777 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41778 | 41778 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41779 | 41779 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
41780 | 41780 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41781 | 41781 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
41782 | 41782 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41783 | 41783 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41784 | 41784 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41785 | 41785 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41786 | 41786 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41787 | 41787 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41788 | 41788 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41789 | 41789 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41790 | 41790 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41791 | 41791 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41792 | 41792 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41793 | 41793 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41794 | 41794 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41795 | 41795 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
41796 | 41796 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
41797 | 41797 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
41798 | 41798 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
41799 | 41799 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
41800 | 41800 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
41801 | 41801 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
41802 | 41802 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
41803 | 41803 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41804 | 41804 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
41805 | 41805 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Tauro ECO 50-3-P Tauro ECO 50-3-P Tauro ECO 99-3-D Tauro ECO 100-3-P Tauro ECO 100-3-D
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (103)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (103) | uint16 |  |  | 103
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (103) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF
6 | 6 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF
7 | 7 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
8 | 8 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF
9 | 9 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF
10 | 10 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF
11 | 11 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
12 | 12 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF
13 | 13 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF
14 | 14 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
15 | 15 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
16 | 16 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
17 | 17 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
20 | 20 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
21 | 21 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
22 | 22 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
23 | 23 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
24 | 24 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
25 | 26 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
27 | 27 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
28 | 28 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF
29 | 29 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | auto-scaled on DCA
30 | 30 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF
31 | 31 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | auto-scaled on DCV
32 | 32 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
33 | 33 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
34 | 34 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
35 | 35 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
39 | 39 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40 | 40 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
41 | 42 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
43 | 44 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
45 | 46 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
47 | 48 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
49 | 50 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
51 | 52 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 28
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 1 MPPT => 1 repeating block
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported

## DERMeasureAC (701)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
3 | 3 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
4 | 4 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
5 | 5 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
6 | 6 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
7 | 8 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
9 | 10 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
11 | 11 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
12 | 12 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
13 | 13 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
14 | 14 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
15 | 15 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
16 | 16 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
17 | 17 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
18 | 19 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
20 | 23 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
24 | 27 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
28 | 31 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
32 | 35 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
39 | 39 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40 | 40 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
41 | 41 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
42 | 42 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
43 | 43 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
44 | 44 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
45 | 45 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
46 | 46 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
47 | 47 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
48 | 48 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
49 | 52 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
53 | 56 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
57 | 60 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
61 | 64 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
65 | 65 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
66 | 66 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
67 | 67 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
68 | 68 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
69 | 69 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
70 | 70 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
71 | 71 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
72 | 75 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
76 | 79 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
80 | 83 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
84 | 87 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
88 | 88 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
89 | 89 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
90 | 90 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
91 | 91 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
92 | 92 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
93 | 93 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
94 | 94 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
95 | 98 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
99 | 102 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
103 | 106 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
107 | 110 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
111 | 111 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
112 | 113 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
114 | 114 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
115 | 115 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
116 | 116 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
117 | 117 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
118 | 118 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
119 | 119 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
120 | 120 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
121 | 121 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
122 | 122 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
123 | 123 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
124 | 155 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported

## DERCapacity (702)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
4 | 4 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
5 | 5 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
6 | 6 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
7 | 7 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
8 | 8 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
9 | 9 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
10 | 10 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
11 | 11 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
12 | 12 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
13 | 13 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
14 | 14 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
15 | 15 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
16 | 16 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
17 | 17 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
19 | 19 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
20 | 20 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
21 | 21 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
22 | 22 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
23 | 23 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
24 | 25 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
26 | 26 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
27 | 27 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
28 | 28 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
29 | 29 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
30 | 30 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
31 | 31 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
32 | 32 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
33 | 33 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
34 | 34 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
35 | 35 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
36 | 36 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
37 | 37 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
38 | 38 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
39 | 39 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40 | 40 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
41 | 41 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
42 | 42 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
43 | 43 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
44 | 44 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
45 | 45 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
46 | 46 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
47 | 47 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
48 | 48 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
49 | 49 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
50 | 50 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
51 | 51 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
52 | 52 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6

## DEREnterService (703)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
3 | 3 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
5 | 5 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
6 | 7 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
8 | 9 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
10 | 11 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
12 | 13 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
14 | 15 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
18 | 18 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2

## DERCtlAC (704)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
3 | 3 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
5 | 6 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
7 | 8 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
9 | 9 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
10 | 10 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
11 | 12 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
13 | 14 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
15 | 15 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
17 | 17 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
18 | 18 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
19 | 20 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
21 | 22 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
23 | 23 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
24 | 24 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
25 | 26 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
27 | 28 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
29 | 29 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
30 | 30 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
31 | 31 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
32 | 33 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
34 | 35 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
36 | 36 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
37 | 37 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
38 | 38 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
39 | 40 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
41 | 42 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
43 | 43 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
46 | 47 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
48 | 49 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
50 | 50 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
51 | 51 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
52 | 52 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
53 | 53 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
54 | 54 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
55 | 55 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
56 | 56 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
57 | 57 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
58 | 58 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
59 | 59 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
60 | 60 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
62 | 62 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
64 | 64 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
65 | 65 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
66 | 66 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
67 | 67 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported

## DERVoltVar (705)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
23 | 24 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
59 | 60 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
66 | 66 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
77 | 78 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
79 | 79 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
80 | 80 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
81 | 81 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
82 | 82 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
83 | 83 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
84 | 84 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
85 | 85 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
86 | 86 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
87 | 87 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERVoltWatt (706)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
29 | 30 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40 | 41 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%

## DERTripLV (707)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHV (708)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripLF (709)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHF (710)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERFreqDroop (711)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
7 | 8 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
9 | 10 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
11 | 11 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
12 | 12 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
13 | 13 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
14 | 14 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
15 | 16 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
17 | 18 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
21 | 22 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
24 | 24 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
27 | 28 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
31 | 32 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
34 | 34 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
35 | 36 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
37 | 38 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
44 | 44 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
45 | 46 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
47 | 48 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
54 | 54 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)

## DERWattVar (712)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
18 | 18 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
34 | 34 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41 | 41 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
50 | 50 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
66 | 66 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
77 | 77 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
78 | 78 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERStorageCapacity (713)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
3 | 3 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
4 | 4 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
5 | 5 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
6 | 6 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
7 | 7 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
8 | 8 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
9 | 9 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0