## Complete Map
Fronius Verto Inverter Register Map with 4 MPPT and Float Inverter Model for US use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 25.0 Verto 27.0 Verto 29.9 Verto 30.0 Verto 33.3 Verto 15.0 208-240 Verto 18.0 208-240 Verto 19.0 208-240 Verto 27.0 480 Verto 30.0 480 Verto 36.0 480
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (113) | uint16 |  |  | 113
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (113) | uint16 | Registers |  | 60
40072 | 40073 | 2 | R | 0x03 | A | AC Current | float32 | A
40074 | 40075 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
40076 | 40077 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A
40078 | 40079 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A
40080 | 40081 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V
40082 | 40083 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V
40084 | 40085 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V
40086 | 40087 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
40088 | 40089 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V
40090 | 40091 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V
40092 | 40093 | 2 | R | 0x03 | W | AC Power | float32 | W
40094 | 40095 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
40096 | 40097 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
40098 | 40099 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
40100 | 40101 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
40102 | 40103 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
40104 | 40105 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40106 | 40107 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40108 | 40109 | 2 | R | 0x03 | DCW | DC Power | float32 | W
40110 | 40111 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
40112 | 40113 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
40114 | 40115 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
40116 | 40117 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
40118 | 40118 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40119 | 40119 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40120 | 40121 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40122 | 40123 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40124 | 40125 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40126 | 40127 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40128 | 40129 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40130 | 40131 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40132 | 40132 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40133 | 40133 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40134 | 40134 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
40135 | 40135 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40136 | 40136 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40137 | 40137 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40138 | 40138 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40139 | 40139 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40140 | 40140 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
40141 | 40141 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
40142 | 40142 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40143 | 40143 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40144 | 40144 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40145 | 40145 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40146 | 40146 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40147 | 40147 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
40148 | 40148 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
40149 | 40149 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40150 | 40150 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40151 | 40151 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
40152 | 40152 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
40153 | 40153 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40154 | 40154 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40155 | 40155 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
40156 | 40156 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
40157 | 40157 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
40158 | 40158 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
40159 | 40159 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40160 | 40160 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40161 | 40161 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40162 | 40162 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40163 | 40163 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40164 | 40164 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40165 | 40165 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40166 | 40166 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40167 | 40167 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40168 | 40168 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40169 | 40169 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40170 | 40170 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40171 | 40171 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40172 | 40172 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40173 | 40173 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40174 | 40174 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40175 | 40175 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40176 | 40176 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40177 | 40177 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40178 | 40178 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40180 | 40180 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40181 | 40181 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40182 | 40182 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40183 | 40183 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40184 | 40184 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40185 | 40185 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40186 | 40186 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40187 | 40187 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40188 | 40188 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40189 | 40189 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40190 | 40190 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40191 | 40191 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40192 | 40192 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40193 | 40193 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40194 | 40194 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40195 | 40195 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40196 | 40196 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40197 | 40200 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40201 | 40204 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40205 | 40208 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40209 | 40212 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40213 | 40216 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40217 | 40220 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40221 | 40221 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40222 | 40222 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40223 | 40223 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40224 | 40224 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40225 | 40226 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40227 | 40228 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40229 | 40232 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40233 | 40234 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40235 | 40235 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40236 | 40236 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40237 | 40237 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40238 | 40238 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40239 | 40239 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40243 | 40243 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40245 | 40245 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40249 | 40249 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40251 | 40251 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40252 | 40252 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40253 | 40253 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40254 | 40254 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40255 | 40255 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40256 | 40256 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40257 | 40257 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40258 | 40258 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40259 | 40259 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40260 | 40260 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40261 | 40261 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40262 | 40262 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40263 | 40263 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40264 | 40264 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40265 | 40265 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 88
40266 | 40266 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40267 | 40267 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40268 | 40268 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40269 | 40269 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40270 | 40271 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40272 | 40272 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 4 MPPT => 4 repeating block
40273 | 40273 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40274 | 40274 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40275 | 40282 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40283 | 40283 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40284 | 40284 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40285 | 40285 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40286 | 40287 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40288 | 40289 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40290 | 40290 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40291 | 40291 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40292 | 40293 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
40294 | 40294 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
40295 | 40302 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40303 | 40303 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
40304 | 40304 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
40305 | 40305 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
40306 | 40307 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40308 | 40309 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40310 | 40310 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
40311 | 40311 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
40312 | 40313 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
40314 | 40314 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
40315 | 40322 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
40323 | 40323 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
40324 | 40324 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
40325 | 40325 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
40326 | 40327 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40328 | 40329 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40330 | 40330 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
40331 | 40331 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
40332 | 40333 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
40334 | 40334 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
40335 | 40342 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'MPPT 4'
40343 | 40343 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF
40344 | 40344 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF
40345 | 40345 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF
40346 | 40347 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40348 | 40349 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40350 | 40350 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
40351 | 40351 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
40352 | 40353 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40354 | 40354 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
40355 | 40355 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
40356 | 40356 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
40357 | 40357 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
40358 | 40358 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
40359 | 40359 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
40360 | 40361 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
40362 | 40363 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
40364 | 40364 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
40365 | 40365 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
40366 | 40366 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
40367 | 40367 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
40368 | 40368 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
40369 | 40369 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
40370 | 40370 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
40371 | 40372 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
40373 | 40376 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
40377 | 40380 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
40381 | 40384 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
40385 | 40388 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
40389 | 40389 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
40390 | 40390 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
40391 | 40391 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
40392 | 40392 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40393 | 40393 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
40394 | 40394 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
40395 | 40395 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
40396 | 40396 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
40397 | 40397 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
40398 | 40398 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
40399 | 40399 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
40400 | 40400 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
40401 | 40401 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
40402 | 40405 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
40406 | 40409 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
40410 | 40413 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
40414 | 40417 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
40418 | 40418 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
40419 | 40419 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
40420 | 40420 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
40421 | 40421 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
40422 | 40422 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
40423 | 40423 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
40424 | 40424 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
40425 | 40428 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
40429 | 40432 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
40433 | 40436 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
40437 | 40440 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
40441 | 40441 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
40442 | 40442 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
40443 | 40443 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
40444 | 40444 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
40445 | 40445 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
40446 | 40446 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
40447 | 40447 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
40448 | 40451 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
40452 | 40455 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
40456 | 40459 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
40460 | 40463 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
40464 | 40464 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
40465 | 40466 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
40467 | 40467 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40468 | 40468 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40469 | 40469 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
40470 | 40470 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40471 | 40471 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
40472 | 40472 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
40473 | 40473 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40474 | 40474 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
40475 | 40475 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
40476 | 40476 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
40477 | 40508 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40509 | 40509 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
40510 | 40510 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
40511 | 40511 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
40512 | 40512 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
40513 | 40513 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40514 | 40514 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
40515 | 40515 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40516 | 40516 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
40517 | 40517 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
40518 | 40518 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
40519 | 40519 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40520 | 40520 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40521 | 40521 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
40522 | 40522 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
40523 | 40523 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
40524 | 40524 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
40525 | 40525 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
40526 | 40526 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
40527 | 40527 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
40528 | 40528 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
40529 | 40529 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
40530 | 40530 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
40531 | 40531 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
40532 | 40533 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
40534 | 40534 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
40535 | 40535 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
40536 | 40536 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
40537 | 40537 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
40538 | 40538 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
40539 | 40539 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
40540 | 40540 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
40541 | 40541 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
40542 | 40542 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
40543 | 40543 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
40544 | 40544 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
40545 | 40545 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
40546 | 40546 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
40547 | 40547 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40548 | 40548 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
40549 | 40549 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
40550 | 40550 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
40551 | 40551 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
40552 | 40552 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
40553 | 40553 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
40554 | 40554 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40555 | 40555 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40556 | 40556 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
40557 | 40557 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40558 | 40558 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40559 | 40559 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40560 | 40560 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40561 | 40561 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
40562 | 40562 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
40563 | 40563 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
40564 | 40564 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
40565 | 40565 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40566 | 40567 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40568 | 40569 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40570 | 40571 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
40572 | 40573 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
40574 | 40575 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
40576 | 40577 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
40578 | 40578 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
40579 | 40579 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40580 | 40580 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
40581 | 40581 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
40582 | 40582 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
40583 | 40583 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40584 | 40585 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40586 | 40587 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40588 | 40588 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
40589 | 40589 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
40590 | 40591 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
40592 | 40593 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
40594 | 40594 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
40595 | 40595 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40596 | 40596 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40597 | 40597 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
40598 | 40599 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
40600 | 40601 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40602 | 40602 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
40603 | 40603 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
40604 | 40605 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
40606 | 40607 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
40608 | 40608 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40609 | 40609 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40610 | 40610 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
40611 | 40612 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
40613 | 40614 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
40615 | 40615 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40616 | 40616 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
40617 | 40617 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
40618 | 40619 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40620 | 40621 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40622 | 40622 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40623 | 40623 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40624 | 40624 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
40625 | 40626 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
40627 | 40628 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40629 | 40629 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
40630 | 40630 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
40631 | 40631 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
40632 | 40632 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
40633 | 40633 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40634 | 40634 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
40635 | 40635 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
40636 | 40636 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
40637 | 40637 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
40638 | 40638 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
40639 | 40639 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40640 | 40640 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40641 | 40641 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40642 | 40642 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40643 | 40643 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40644 | 40644 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
40645 | 40645 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40646 | 40646 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40647 | 40647 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
40648 | 40648 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
40649 | 40649 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40650 | 40650 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40651 | 40651 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40652 | 40652 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
40653 | 40653 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40654 | 40655 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40656 | 40657 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40658 | 40658 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40659 | 40659 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40660 | 40660 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
40661 | 40661 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
40662 | 40662 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
40663 | 40663 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40664 | 40664 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
40665 | 40665 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40666 | 40666 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40667 | 40667 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40668 | 40668 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40669 | 40670 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40671 | 40671 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40672 | 40672 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40673 | 40673 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40674 | 40674 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40675 | 40675 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40676 | 40676 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40677 | 40677 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40678 | 40678 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40679 | 40679 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40680 | 40680 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
40681 | 40681 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40682 | 40682 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
40683 | 40683 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40684 | 40684 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40685 | 40685 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40686 | 40686 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40687 | 40688 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40689 | 40689 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40690 | 40690 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40691 | 40691 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40692 | 40692 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40693 | 40693 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40694 | 40694 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40695 | 40695 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40696 | 40696 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40697 | 40697 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40698 | 40698 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
40699 | 40699 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40700 | 40700 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
40701 | 40701 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40702 | 40702 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40703 | 40703 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40704 | 40704 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40705 | 40706 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40707 | 40707 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40708 | 40708 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40709 | 40709 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40710 | 40710 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40711 | 40711 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40712 | 40712 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40713 | 40713 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40714 | 40714 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40715 | 40715 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40716 | 40716 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
40717 | 40717 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40718 | 40718 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
40719 | 40719 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40720 | 40720 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40721 | 40721 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40722 | 40722 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40723 | 40724 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40725 | 40725 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40726 | 40726 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40727 | 40727 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40728 | 40728 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40729 | 40729 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40730 | 40730 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40731 | 40731 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40732 | 40732 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40733 | 40733 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40734 | 40734 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
40735 | 40735 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
40736 | 40736 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40737 | 40737 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40738 | 40738 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40739 | 40739 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
40740 | 40740 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40741 | 40742 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40743 | 40744 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40745 | 40745 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40746 | 40746 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40747 | 40747 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
40748 | 40748 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
40749 | 40749 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40750 | 40750 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40751 | 40752 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40753 | 40753 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40754 | 40754 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40755 | 40755 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40756 | 40756 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40757 | 40757 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40758 | 40758 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40759 | 40759 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40760 | 40760 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40761 | 40761 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40762 | 40763 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40764 | 40764 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40765 | 40765 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40766 | 40766 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40767 | 40767 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40768 | 40768 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40769 | 40769 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40770 | 40770 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40771 | 40771 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40772 | 40772 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40773 | 40774 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40775 | 40775 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40776 | 40776 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40777 | 40777 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40778 | 40778 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40779 | 40779 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40780 | 40780 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40781 | 40781 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40782 | 40782 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40783 | 40783 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40784 | 40785 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40786 | 40786 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40787 | 40787 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40788 | 40788 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40789 | 40789 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40790 | 40790 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40791 | 40791 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40792 | 40792 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40793 | 40793 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
40794 | 40794 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
40795 | 40795 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40796 | 40796 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40797 | 40797 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40798 | 40798 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40799 | 40799 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40800 | 40800 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40801 | 40801 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40802 | 40802 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40803 | 40803 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40804 | 40804 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40805 | 40806 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40807 | 40807 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40808 | 40809 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40810 | 40810 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40811 | 40812 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40813 | 40813 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40814 | 40815 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40816 | 40816 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40817 | 40818 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40819 | 40819 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40820 | 40820 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40821 | 40822 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40823 | 40823 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40824 | 40825 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40826 | 40826 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40827 | 40828 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40829 | 40829 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40830 | 40831 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40832 | 40832 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40833 | 40834 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40835 | 40835 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40836 | 40836 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40837 | 40838 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40839 | 40839 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40840 | 40841 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40842 | 40842 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40843 | 40844 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40845 | 40845 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40846 | 40847 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40848 | 40848 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40849 | 40850 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40851 | 40851 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40852 | 40852 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40853 | 40853 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40854 | 40855 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40856 | 40856 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40857 | 40858 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40859 | 40859 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40860 | 40861 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40862 | 40862 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40863 | 40864 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40865 | 40865 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40866 | 40867 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40868 | 40868 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40869 | 40869 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40870 | 40871 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40872 | 40872 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40873 | 40874 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40875 | 40875 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40876 | 40877 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40878 | 40878 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40879 | 40880 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40881 | 40881 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40882 | 40883 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40884 | 40884 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40885 | 40885 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40886 | 40887 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40888 | 40888 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40889 | 40890 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40891 | 40891 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40892 | 40893 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40894 | 40894 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40895 | 40896 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40897 | 40897 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40898 | 40899 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40900 | 40900 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40901 | 40901 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40902 | 40902 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40903 | 40904 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40905 | 40905 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40906 | 40907 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40908 | 40908 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40909 | 40910 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40911 | 40911 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40912 | 40913 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40914 | 40914 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40915 | 40916 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40917 | 40917 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40918 | 40918 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40919 | 40920 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40921 | 40921 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40922 | 40923 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40924 | 40924 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40925 | 40926 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40927 | 40927 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40928 | 40929 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40930 | 40930 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40931 | 40932 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40933 | 40933 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40934 | 40934 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40935 | 40936 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40937 | 40937 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40938 | 40939 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40940 | 40940 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40941 | 40942 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40943 | 40943 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40944 | 40945 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40946 | 40946 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40947 | 40948 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40949 | 40949 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40950 | 40950 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40951 | 40951 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40952 | 40953 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40954 | 40954 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40955 | 40956 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40957 | 40957 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40958 | 40959 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40960 | 40960 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40961 | 40962 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40963 | 40963 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40964 | 40965 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40966 | 40966 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40967 | 40967 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40968 | 40969 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40970 | 40970 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40971 | 40972 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40973 | 40973 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40974 | 40975 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40976 | 40976 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40977 | 40978 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40979 | 40979 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40980 | 40981 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40982 | 40982 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40983 | 40983 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40984 | 40985 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40986 | 40986 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40987 | 40988 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40989 | 40989 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40990 | 40991 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40992 | 40992 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40993 | 40994 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40995 | 40995 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40996 | 40997 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40998 | 40998 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
40999 | 40999 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
41000 | 41000 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41001 | 41001 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41002 | 41002 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41003 | 41003 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41004 | 41004 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41005 | 41005 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
41006 | 41006 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41007 | 41007 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41008 | 41008 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41009 | 41009 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41010 | 41011 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41012 | 41012 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41013 | 41014 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41015 | 41015 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41016 | 41017 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41018 | 41018 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41019 | 41020 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41021 | 41021 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41022 | 41023 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41024 | 41024 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41025 | 41025 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41026 | 41027 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41028 | 41028 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41029 | 41030 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41031 | 41031 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41032 | 41033 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41034 | 41034 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41035 | 41036 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41037 | 41037 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41038 | 41039 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41040 | 41040 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41041 | 41041 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41042 | 41043 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41044 | 41044 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41045 | 41046 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41047 | 41047 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41048 | 41049 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41050 | 41050 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41051 | 41052 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41053 | 41053 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41054 | 41055 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41056 | 41056 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41057 | 41057 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41058 | 41058 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41059 | 41060 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41061 | 41061 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41062 | 41063 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41064 | 41064 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41065 | 41066 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41067 | 41067 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41068 | 41069 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41070 | 41070 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41071 | 41072 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41073 | 41073 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41074 | 41074 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41075 | 41076 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41077 | 41077 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41078 | 41079 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41080 | 41080 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41081 | 41082 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41083 | 41083 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41084 | 41085 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41086 | 41086 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41087 | 41088 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41089 | 41089 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41090 | 41090 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41091 | 41092 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41093 | 41093 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41094 | 41095 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41096 | 41096 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41097 | 41098 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41099 | 41099 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41100 | 41101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41102 | 41102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41103 | 41104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41105 | 41105 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41106 | 41106 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41107 | 41107 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41108 | 41109 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41110 | 41110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41111 | 41112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41113 | 41113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41114 | 41115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41116 | 41116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41117 | 41118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41119 | 41119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41120 | 41121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41122 | 41122 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41123 | 41123 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41124 | 41125 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41126 | 41126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41127 | 41128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41129 | 41129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41130 | 41131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41132 | 41132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41133 | 41134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41135 | 41135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41136 | 41137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41138 | 41138 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41139 | 41139 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41140 | 41141 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41142 | 41142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41143 | 41144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41145 | 41145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41146 | 41147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41148 | 41148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41149 | 41150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41151 | 41151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41152 | 41153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41154 | 41154 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41155 | 41155 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41156 | 41156 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41157 | 41158 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41159 | 41159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41160 | 41161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41162 | 41162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41163 | 41164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41165 | 41165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41166 | 41167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41168 | 41168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41169 | 41170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41171 | 41171 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41172 | 41172 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41173 | 41174 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41175 | 41175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41176 | 41177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41178 | 41178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41179 | 41180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41181 | 41181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41182 | 41183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41184 | 41184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41185 | 41186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41187 | 41187 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41188 | 41188 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41189 | 41190 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41191 | 41191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41192 | 41193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41194 | 41194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41195 | 41196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41197 | 41197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41198 | 41199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41200 | 41200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41201 | 41202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41203 | 41203 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
41204 | 41204 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
41205 | 41205 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41206 | 41206 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41207 | 41207 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41208 | 41208 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41209 | 41209 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41210 | 41210 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41211 | 41211 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41212 | 41212 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41213 | 41213 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41214 | 41215 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41216 | 41217 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41218 | 41219 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41220 | 41221 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41222 | 41223 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41224 | 41225 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41226 | 41227 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41228 | 41229 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41230 | 41231 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41232 | 41233 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41234 | 41234 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41235 | 41236 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41237 | 41238 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41239 | 41240 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41241 | 41242 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41243 | 41244 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41245 | 41246 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41247 | 41248 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41249 | 41250 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41251 | 41252 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41253 | 41254 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41255 | 41255 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41256 | 41257 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41258 | 41259 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41260 | 41261 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41262 | 41263 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41264 | 41265 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41266 | 41267 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41268 | 41269 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41270 | 41271 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41272 | 41273 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41274 | 41275 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41276 | 41276 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41277 | 41277 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41278 | 41279 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41280 | 41281 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41282 | 41283 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41284 | 41285 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41286 | 41287 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41288 | 41289 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41290 | 41291 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41292 | 41293 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41294 | 41295 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41296 | 41297 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41298 | 41298 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41299 | 41300 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41301 | 41302 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41303 | 41304 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41305 | 41306 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41307 | 41308 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41309 | 41310 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41311 | 41312 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41313 | 41314 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41315 | 41316 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41317 | 41318 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41319 | 41319 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41320 | 41321 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41322 | 41323 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41324 | 41325 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41326 | 41327 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41328 | 41329 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41330 | 41331 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41332 | 41333 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41334 | 41335 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41336 | 41337 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41338 | 41339 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41340 | 41340 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41341 | 41341 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41342 | 41343 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41344 | 41345 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41346 | 41347 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41348 | 41349 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41350 | 41351 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41352 | 41353 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41354 | 41355 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41356 | 41357 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41358 | 41359 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41360 | 41361 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41362 | 41362 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41363 | 41364 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41365 | 41366 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41367 | 41368 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41369 | 41370 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41371 | 41372 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41373 | 41374 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41375 | 41376 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41377 | 41378 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41379 | 41380 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41381 | 41382 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41383 | 41383 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41384 | 41385 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41386 | 41387 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41388 | 41389 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41390 | 41391 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41392 | 41393 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41394 | 41395 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41396 | 41397 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41398 | 41399 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41400 | 41401 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41402 | 41403 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41404 | 41404 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41405 | 41405 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41406 | 41407 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41408 | 41409 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41410 | 41411 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41412 | 41413 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41414 | 41415 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41416 | 41417 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41418 | 41419 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41420 | 41421 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41422 | 41423 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41424 | 41425 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41426 | 41426 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41427 | 41428 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41429 | 41430 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41431 | 41432 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41433 | 41434 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41435 | 41436 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41437 | 41438 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41439 | 41440 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41441 | 41442 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41443 | 41444 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41445 | 41446 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41447 | 41447 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41448 | 41449 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41450 | 41451 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41452 | 41453 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41454 | 41455 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41456 | 41457 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41458 | 41459 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41460 | 41461 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41462 | 41463 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41464 | 41465 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41466 | 41467 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41468 | 41468 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
41469 | 41469 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
41470 | 41470 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41471 | 41471 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41472 | 41472 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41473 | 41473 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41474 | 41474 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41475 | 41475 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41476 | 41476 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41477 | 41477 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41478 | 41478 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41479 | 41480 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41481 | 41482 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41483 | 41484 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41485 | 41486 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41487 | 41488 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41489 | 41490 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41491 | 41492 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41493 | 41494 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41495 | 41496 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41497 | 41498 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41499 | 41499 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41500 | 41501 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41502 | 41503 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41504 | 41505 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41506 | 41507 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41508 | 41509 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41510 | 41511 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41512 | 41513 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41514 | 41515 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41516 | 41517 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41518 | 41519 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41520 | 41520 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41521 | 41522 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41523 | 41524 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41525 | 41526 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41527 | 41528 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41529 | 41530 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41531 | 41532 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41533 | 41534 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41535 | 41536 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41537 | 41538 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41539 | 41540 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41541 | 41541 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41542 | 41542 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41543 | 41544 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41545 | 41546 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41547 | 41548 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41549 | 41550 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41551 | 41552 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41553 | 41554 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41555 | 41556 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41557 | 41558 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41559 | 41560 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41561 | 41562 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41563 | 41563 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41564 | 41565 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41566 | 41567 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41568 | 41569 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41570 | 41571 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41572 | 41573 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41574 | 41575 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41576 | 41577 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41578 | 41579 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41580 | 41581 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41582 | 41583 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41584 | 41584 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41585 | 41586 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41587 | 41588 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41589 | 41590 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41591 | 41592 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41593 | 41594 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41595 | 41596 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41597 | 41598 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41599 | 41600 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41601 | 41602 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41603 | 41604 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41605 | 41605 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41606 | 41606 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41607 | 41608 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41609 | 41610 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41611 | 41612 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41613 | 41614 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41615 | 41616 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41617 | 41618 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41619 | 41620 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41621 | 41622 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41623 | 41624 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41625 | 41626 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41627 | 41627 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41628 | 41629 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41630 | 41631 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41632 | 41633 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41634 | 41635 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41636 | 41637 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41638 | 41639 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41640 | 41641 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41642 | 41643 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41644 | 41645 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41646 | 41647 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41648 | 41648 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41649 | 41650 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41651 | 41652 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41653 | 41654 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41655 | 41656 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41657 | 41658 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41659 | 41660 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41661 | 41662 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41663 | 41664 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41665 | 41666 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41667 | 41668 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41669 | 41669 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41670 | 41670 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41671 | 41672 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41673 | 41674 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41675 | 41676 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41677 | 41678 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41679 | 41680 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41681 | 41682 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41683 | 41684 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41685 | 41686 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41687 | 41688 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41689 | 41690 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41691 | 41691 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41692 | 41693 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41694 | 41695 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41696 | 41697 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41698 | 41699 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41700 | 41701 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41702 | 41703 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41704 | 41705 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41706 | 41707 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41708 | 41709 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41710 | 41711 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41712 | 41712 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41713 | 41714 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41715 | 41716 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41717 | 41718 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41719 | 41720 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41721 | 41722 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41723 | 41724 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41725 | 41726 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41727 | 41728 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41729 | 41730 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41731 | 41732 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41733 | 41733 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
41734 | 41734 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
41735 | 41735 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41736 | 41736 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
41737 | 41737 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41738 | 41738 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
41739 | 41740 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41741 | 41742 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41743 | 41743 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
41744 | 41744 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
41745 | 41745 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
41746 | 41746 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
41747 | 41748 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41749 | 41750 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41751 | 41751 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41752 | 41752 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41753 | 41754 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41755 | 41755 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41756 | 41756 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
41757 | 41758 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41759 | 41760 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41761 | 41761 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41762 | 41762 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41763 | 41764 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41765 | 41765 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41766 | 41766 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41767 | 41768 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41769 | 41770 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41771 | 41771 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41772 | 41772 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41773 | 41774 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41775 | 41775 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41776 | 41776 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41777 | 41778 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41779 | 41780 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41781 | 41781 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41782 | 41782 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41783 | 41784 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41785 | 41785 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41786 | 41786 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41787 | 41787 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
41788 | 41788 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
41789 | 41789 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41790 | 41790 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
41791 | 41791 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41792 | 41792 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
41793 | 41793 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
41794 | 41795 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41796 | 41797 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41798 | 41798 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
41799 | 41799 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
41800 | 41800 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
41801 | 41801 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
41802 | 41802 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41803 | 41803 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
41804 | 41804 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41805 | 41805 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41806 | 41806 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41807 | 41807 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41808 | 41808 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41809 | 41809 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41810 | 41810 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41811 | 41811 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41812 | 41812 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41813 | 41813 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41814 | 41814 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41815 | 41815 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41816 | 41816 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41817 | 41817 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
41818 | 41818 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41819 | 41819 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
41820 | 41820 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41821 | 41821 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41822 | 41822 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41823 | 41823 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41824 | 41824 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41825 | 41825 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41826 | 41826 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41827 | 41827 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41828 | 41828 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41829 | 41829 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41830 | 41830 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41831 | 41831 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41832 | 41832 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41833 | 41833 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
41834 | 41834 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41835 | 41835 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
41836 | 41836 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41837 | 41837 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41838 | 41838 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41839 | 41839 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41840 | 41840 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41841 | 41841 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41842 | 41842 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41843 | 41843 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41844 | 41844 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41845 | 41845 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41846 | 41846 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41847 | 41847 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41848 | 41848 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41849 | 41849 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
41850 | 41850 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41851 | 41851 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
41852 | 41852 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41853 | 41853 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41854 | 41854 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41855 | 41855 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41856 | 41856 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41857 | 41857 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41858 | 41858 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41859 | 41859 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41860 | 41860 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41861 | 41861 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41862 | 41862 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41863 | 41863 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41864 | 41864 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41865 | 41865 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
41866 | 41866 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
41867 | 41867 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
41868 | 41868 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
41869 | 41869 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
41870 | 41870 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
41871 | 41871 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
41872 | 41872 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
41873 | 41873 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41874 | 41874 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
41875 | 41875 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 25.0 Verto 27.0 Verto 29.9 Verto 30.0 Verto 33.3 Verto 15.0 208-240 Verto 18.0 208-240 Verto 19.0 208-240 Verto 27.0 480 Verto 30.0 480 Verto 36.0 480
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (113)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (113) | uint16 |  |  | 113
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (113) | uint16 | Registers |  | 60
3 | 4 | 2 | R | 0x03 | A | AC Current | float32 | A
5 | 6 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
7 | 8 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A
9 | 10 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A
11 | 12 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V
13 | 14 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V
15 | 16 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V
17 | 18 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
19 | 20 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V
21 | 22 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V
23 | 24 | 2 | R | 0x03 | W | AC Power | float32 | W
25 | 26 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
27 | 28 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
29 | 30 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
31 | 32 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
33 | 34 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
35 | 36 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
37 | 38 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
39 | 40 | 2 | R | 0x03 | DCW | DC Power | float32 | W
41 | 42 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
43 | 44 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
45 | 46 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
47 | 48 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
49 | 49 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
50 | 50 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
51 | 52 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
53 | 54 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
55 | 56 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
57 | 58 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
59 | 60 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
61 | 62 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 88
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 4 MPPT => 4 repeating block
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
31 | 31 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40 | 40 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
41 | 41 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
42 | 42 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
43 | 44 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
45 | 46 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
47 | 47 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
48 | 48 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
49 | 50 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
51 | 51 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
52 | 59 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
60 | 60 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
61 | 61 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
62 | 62 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
63 | 64 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
65 | 66 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
67 | 67 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
68 | 68 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
69 | 70 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
71 | 71 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
72 | 79 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'MPPT 4'
80 | 80 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF
81 | 81 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF
82 | 82 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF
83 | 84 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
85 | 86 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
87 | 87 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
88 | 88 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
89 | 90 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported

## DERMeasureAC (701)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
3 | 3 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
4 | 4 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
5 | 5 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
6 | 6 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
7 | 8 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
9 | 10 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
11 | 11 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
12 | 12 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
13 | 13 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
14 | 14 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
15 | 15 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
16 | 16 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
17 | 17 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
18 | 19 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
20 | 23 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
24 | 27 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
28 | 31 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
32 | 35 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
39 | 39 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40 | 40 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
41 | 41 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
42 | 42 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
43 | 43 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
44 | 44 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
45 | 45 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
46 | 46 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
47 | 47 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
48 | 48 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
49 | 52 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
53 | 56 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
57 | 60 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
61 | 64 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
65 | 65 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
66 | 66 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
67 | 67 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
68 | 68 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
69 | 69 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
70 | 70 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
71 | 71 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
72 | 75 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
76 | 79 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
80 | 83 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
84 | 87 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
88 | 88 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
89 | 89 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
90 | 90 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
91 | 91 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
92 | 92 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
93 | 93 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
94 | 94 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
95 | 98 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
99 | 102 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
103 | 106 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
107 | 110 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
111 | 111 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
112 | 113 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
114 | 114 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
115 | 115 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
116 | 116 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
117 | 117 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
118 | 118 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
119 | 119 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
120 | 120 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
121 | 121 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
122 | 122 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
123 | 123 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
124 | 155 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported

## DERCapacity (702)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
4 | 4 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
5 | 5 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
6 | 6 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
7 | 7 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
8 | 8 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
9 | 9 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
10 | 10 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
11 | 11 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
12 | 12 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
13 | 13 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
14 | 14 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
15 | 15 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
16 | 16 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
17 | 17 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
19 | 19 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
20 | 20 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
21 | 21 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
22 | 22 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
23 | 23 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
24 | 25 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
26 | 26 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
27 | 27 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
28 | 28 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
29 | 29 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
30 | 30 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
31 | 31 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
32 | 32 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
33 | 33 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
34 | 34 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
35 | 35 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
36 | 36 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
37 | 37 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
38 | 38 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
39 | 39 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40 | 40 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
41 | 41 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
42 | 42 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
43 | 43 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
44 | 44 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
45 | 45 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
46 | 46 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
47 | 47 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
48 | 48 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
49 | 49 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
50 | 50 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
51 | 51 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
52 | 52 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6

## DEREnterService (703)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
3 | 3 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
5 | 5 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
6 | 7 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
8 | 9 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
10 | 11 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
12 | 13 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
14 | 15 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
18 | 18 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2

## DERCtlAC (704)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
3 | 3 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
5 | 6 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
7 | 8 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
9 | 9 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
10 | 10 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
11 | 12 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
13 | 14 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
15 | 15 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
17 | 17 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
18 | 18 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
19 | 20 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
21 | 22 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
23 | 23 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
24 | 24 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
25 | 26 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
27 | 28 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
29 | 29 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
30 | 30 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
31 | 31 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
32 | 33 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
34 | 35 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
36 | 36 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
37 | 37 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
38 | 38 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
39 | 40 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
41 | 42 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
43 | 43 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
46 | 47 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
48 | 49 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
50 | 50 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
51 | 51 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
52 | 52 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
53 | 53 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
54 | 54 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
55 | 55 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
56 | 56 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
57 | 57 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
58 | 58 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
59 | 59 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
60 | 60 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
62 | 62 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
64 | 64 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
65 | 65 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
66 | 66 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
67 | 67 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported

## DERVoltVar (705)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
23 | 24 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
59 | 60 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
66 | 66 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
77 | 78 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
79 | 79 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
80 | 80 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
81 | 81 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
82 | 82 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
83 | 83 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
84 | 84 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
85 | 85 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
86 | 86 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
87 | 87 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERVoltWatt (706)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
29 | 30 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40 | 41 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%

## DERTripLV (707)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHV (708)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripLF (709)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHF (710)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERFreqDroop (711)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
7 | 8 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
9 | 10 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
11 | 11 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
12 | 12 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
13 | 13 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
14 | 14 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
15 | 16 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
17 | 18 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
21 | 22 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
24 | 24 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
27 | 28 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
31 | 32 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
34 | 34 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
35 | 36 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
37 | 38 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
44 | 44 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
45 | 46 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
47 | 48 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
54 | 54 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)

## DERWattVar (712)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
18 | 18 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
34 | 34 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41 | 41 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
50 | 50 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
66 | 66 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
77 | 77 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
78 | 78 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERStorageCapacity (713)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
3 | 3 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
4 | 4 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
5 | 5 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
6 | 6 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
7 | 7 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
8 | 8 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
9 | 9 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0