## Complete Map
Fronius Verto Inverter Register Map with 4 MPPT, Float Inverter Model and storage configured for US use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 25.0 Verto 27.0 Verto 29.9 Verto 30.0 Verto 33.3 Verto 15.0 208-240 Verto 18.0 208-240 Verto 19.0 208-240 Verto 27.0 480 Verto 30.0 480 Verto 36.0 480
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (113) | uint16 |  |  | 113
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (113) | uint16 | Registers |  | 60
40072 | 40073 | 2 | R | 0x03 | A | AC Current | float32 | A
40074 | 40075 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
40076 | 40077 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A
40078 | 40079 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A
40080 | 40081 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V
40082 | 40083 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V
40084 | 40085 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V
40086 | 40087 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
40088 | 40089 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V
40090 | 40091 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V
40092 | 40093 | 2 | R | 0x03 | W | AC Power | float32 | W
40094 | 40095 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
40096 | 40097 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
40098 | 40099 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
40100 | 40101 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
40102 | 40103 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
40104 | 40105 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40106 | 40107 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40108 | 40109 | 2 | R | 0x03 | DCW | DC Power | float32 | W
40110 | 40111 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
40112 | 40113 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
40114 | 40115 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
40116 | 40117 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
40118 | 40118 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40119 | 40119 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40120 | 40121 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40122 | 40123 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40124 | 40125 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40126 | 40127 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40128 | 40129 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40130 | 40131 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40132 | 40132 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40133 | 40133 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40134 | 40134 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 82 (PV_STOR)
40135 | 40135 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40136 | 40136 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40137 | 40137 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40138 | 40138 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40139 | 40139 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40140 | 40140 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF
40141 | 40141 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF
40142 | 40142 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40143 | 40143 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40144 | 40144 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40145 | 40145 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40146 | 40146 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40147 | 40147 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40148 | 40148 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40149 | 40149 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40150 | 40150 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40151 | 40151 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
40152 | 40152 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf
40153 | 40153 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40154 | 40154 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40155 | 40155 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
40156 | 40156 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
40157 | 40157 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
40158 | 40158 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
40159 | 40159 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40160 | 40160 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40161 | 40161 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40162 | 40162 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40163 | 40163 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40164 | 40164 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40165 | 40165 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40166 | 40166 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40167 | 40167 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40168 | 40168 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40169 | 40169 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40170 | 40170 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40171 | 40171 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40172 | 40172 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40173 | 40173 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40174 | 40174 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40175 | 40175 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40176 | 40176 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40177 | 40177 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40178 | 40178 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40180 | 40180 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40181 | 40181 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40182 | 40182 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40183 | 40183 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40184 | 40184 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40185 | 40185 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40186 | 40186 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40187 | 40187 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40188 | 40188 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40189 | 40189 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40190 | 40190 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40191 | 40191 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40192 | 40192 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40193 | 40193 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40194 | 40194 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40195 | 40195 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40196 | 40196 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40197 | 40200 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40201 | 40204 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40205 | 40208 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40209 | 40212 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40213 | 40216 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40217 | 40220 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40221 | 40221 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40222 | 40222 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40223 | 40223 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40224 | 40224 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40225 | 40226 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40227 | 40228 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40229 | 40232 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40233 | 40234 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40235 | 40235 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40236 | 40236 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40237 | 40237 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40238 | 40238 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40239 | 40239 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40243 | 40243 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40245 | 40245 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40249 | 40249 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40251 | 40251 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40252 | 40252 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40253 | 40253 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40254 | 40254 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40255 | 40255 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40256 | 40256 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40257 | 40257 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40258 | 40258 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40259 | 40259 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40260 | 40260 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40261 | 40261 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40262 | 40262 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40263 | 40263 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40264 | 40264 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40265 | 40265 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 128
40266 | 40266 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40267 | 40267 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40268 | 40268 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40269 | 40269 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40270 | 40271 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40272 | 40272 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers + 2 * number of battery inputs 4 MPPT and 1 BATTERY => 6 repeating blocks
40273 | 40273 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40274 | 40274 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40275 | 40282 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40283 | 40283 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40284 | 40284 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40285 | 40285 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40286 | 40287 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40288 | 40289 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40290 | 40290 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40291 | 40291 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40292 | 40293 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
40294 | 40294 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
40295 | 40302 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40303 | 40303 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
40304 | 40304 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
40305 | 40305 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
40306 | 40307 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40308 | 40309 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40310 | 40310 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
40311 | 40311 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
40312 | 40313 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
40314 | 40314 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
40315 | 40322 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
40323 | 40323 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
40324 | 40324 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
40325 | 40325 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
40326 | 40327 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40328 | 40329 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40330 | 40330 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
40331 | 40331 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
40332 | 40333 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
40334 | 40334 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
40335 | 40342 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'MPPT 4'
40343 | 40343 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF
40344 | 40344 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF
40345 | 40345 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF
40346 | 40347 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40348 | 40349 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40350 | 40350 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
40351 | 40351 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
40352 | 40353 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported
40354 | 40354 | 1 | R | 0x03 | module/5/ID | Input ID | uint16 |  |  | 5
40355 | 40362 | 8 | R | 0x03 | module/5/IDStr | Input ID Sting | string |  |  | 'StCha 5'
40363 | 40363 | 1 | R | 0x03 | module/5/DCA | DC Current | uint16 | A | DCA_SF | When the battery is discharged the data-points of the charge input are set to 0
40364 | 40364 | 1 | R | 0x03 | module/5/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
40365 | 40365 | 1 | R | 0x03 | module/5/DCW | DC Power | uint16 | W | DCW_SF | When the battery is discharged the data-points of the charge input are set to 0
40366 | 40367 | 2 | R | 0x03 | module/5/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Charge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
40368 | 40369 | 2 | R | 0x03 | module/5/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40370 | 40370 | 1 | R | 0x03 | module/5/Tmp | Temperature | int16 | C |  | not supported
40371 | 40371 | 1 | R | 0x03 | module/5/DCSt | Operating State | enum16 |  |  | not supported
40372 | 40373 | 2 | R | 0x03 | module/5/DCEvt | Module Events | bitfield32 |  |  | not supported
40374 | 40374 | 1 | R | 0x03 | module/6/ID | Input ID | uint16 |  |  | 6
40375 | 40382 | 8 | R | 0x03 | module/6/IDStr | Input ID Sting | string |  |  | 'StDisCha 6'
40383 | 40383 | 1 | R | 0x03 | module/6/DCA | DC Current | uint16 | A | DCA_SF | When the battery is charged the data-points of the discharge input are set to 0
40384 | 40384 | 1 | R | 0x03 | module/6/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
40385 | 40385 | 1 | R | 0x03 | module/6/DCW | DC Power | uint16 | W | DCW_SF | When the battery is charged the data-points of the discharge input are set to 0
40386 | 40387 | 2 | R | 0x03 | module/6/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Discharge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
40388 | 40389 | 2 | R | 0x03 | module/6/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40390 | 40390 | 1 | R | 0x03 | module/6/Tmp | Temperature | int16 | C |  | not supported
40391 | 40391 | 1 | R | 0x03 | module/6/DCSt | Operating State | enum16 |  |  | not supported
40392 | 40393 | 2 | R | 0x03 | module/6/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40394 | 40394 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model storage (124) | uint16 |  |  | 124
40395 | 40395 | 1 | R | 0x03 | L | Length of sunspec model storage (124) | uint16 | Registers |  | 24
40396 | 40396 | 1 | R | 0x03 | WChaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. The inverter is not fully capable of transferring power as reported by this reference value. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only | uint16 | W | WChaMax_SF
40397 | 40397 | 1 | R | 0x03 | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
40398 | 40398 | 1 | R | 0x03 | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
40399 | 40399 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
40400 | 40400 | 1 | R | 0x03 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF | not supported
40401 | 40401 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
40402 | 40402 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
40403 | 40403 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | not supported
40404 | 40404 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | not supported
40405 | 40405 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
40406 | 40406 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and WChaMax defines max. Discharge rate. See WChaMax for details | int16 | % WDisChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40407 | 40407 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and WChaMax defines max. Charge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40408 | 40408 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | not supported
40409 | 40409 | 1 | RW | 0x03 0x06 0x10 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | 0 - 28800
40410 | 40410 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | not supported
40411 | 40411 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet |  | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
40412 | 40412 | 1 | R | 0x03 | WChaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
40413 | 40413 | 1 | R | 0x03 | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
40414 | 40414 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | not supported
40415 | 40415 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
40416 | 40416 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
40417 | 40417 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | not supported
40418 | 40418 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | not supported
40419 | 40419 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40420 | 40420 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
40421 | 40421 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
40422 | 40422 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
40423 | 40423 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
40424 | 40424 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
40425 | 40425 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
40426 | 40427 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
40428 | 40429 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
40430 | 40430 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
40431 | 40431 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
40432 | 40432 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
40433 | 40433 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
40434 | 40434 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
40435 | 40435 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
40436 | 40436 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
40437 | 40438 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
40439 | 40442 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
40443 | 40446 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
40447 | 40450 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
40451 | 40454 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
40455 | 40455 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
40456 | 40456 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
40457 | 40457 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
40458 | 40458 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40459 | 40459 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
40460 | 40460 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
40461 | 40461 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
40462 | 40462 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
40463 | 40463 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
40464 | 40464 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
40465 | 40465 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
40466 | 40466 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
40467 | 40467 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
40468 | 40471 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
40472 | 40475 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
40476 | 40479 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
40480 | 40483 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
40484 | 40484 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
40485 | 40485 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
40486 | 40486 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
40487 | 40487 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
40488 | 40488 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
40489 | 40489 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
40490 | 40490 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
40491 | 40494 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
40495 | 40498 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
40499 | 40502 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
40503 | 40506 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
40507 | 40507 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
40508 | 40508 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
40509 | 40509 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
40510 | 40510 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
40511 | 40511 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
40512 | 40512 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
40513 | 40513 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
40514 | 40517 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
40518 | 40521 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
40522 | 40525 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
40526 | 40529 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
40530 | 40530 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
40531 | 40532 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
40533 | 40533 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40534 | 40534 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40535 | 40535 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
40536 | 40536 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40537 | 40537 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
40538 | 40538 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
40539 | 40539 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40540 | 40540 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
40541 | 40541 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
40542 | 40542 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
40543 | 40574 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40575 | 40575 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
40576 | 40576 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
40577 | 40577 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
40578 | 40578 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
40579 | 40579 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40580 | 40580 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
40581 | 40581 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40582 | 40582 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
40583 | 40583 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
40584 | 40584 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
40585 | 40585 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40586 | 40586 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40587 | 40587 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
40588 | 40588 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
40589 | 40589 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
40590 | 40590 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
40591 | 40591 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
40592 | 40592 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
40593 | 40593 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
40594 | 40594 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
40595 | 40595 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
40596 | 40596 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
40597 | 40597 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
40598 | 40599 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
40600 | 40600 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
40601 | 40601 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
40602 | 40602 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
40603 | 40603 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
40604 | 40604 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
40605 | 40605 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
40606 | 40606 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
40607 | 40607 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
40608 | 40608 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
40609 | 40609 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
40610 | 40610 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
40611 | 40611 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
40612 | 40612 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
40613 | 40613 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40614 | 40614 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
40615 | 40615 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
40616 | 40616 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
40617 | 40617 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
40618 | 40618 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
40619 | 40619 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
40620 | 40620 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40621 | 40621 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40622 | 40622 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
40623 | 40623 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40624 | 40624 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40625 | 40625 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40626 | 40626 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40627 | 40627 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
40628 | 40628 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
40629 | 40629 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
40630 | 40630 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
40631 | 40631 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40632 | 40633 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40634 | 40635 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40636 | 40637 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
40638 | 40639 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
40640 | 40641 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
40642 | 40643 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
40644 | 40644 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
40645 | 40645 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40646 | 40646 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
40647 | 40647 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
40648 | 40648 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
40649 | 40649 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40650 | 40651 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40652 | 40653 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40654 | 40654 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
40655 | 40655 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
40656 | 40657 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
40658 | 40659 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
40660 | 40660 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
40661 | 40661 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40662 | 40662 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40663 | 40663 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
40664 | 40665 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
40666 | 40667 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40668 | 40668 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
40669 | 40669 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
40670 | 40671 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
40672 | 40673 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
40674 | 40674 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40675 | 40675 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40676 | 40676 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
40677 | 40678 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
40679 | 40680 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
40681 | 40681 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40682 | 40682 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
40683 | 40683 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
40684 | 40685 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40686 | 40687 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40688 | 40688 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40689 | 40689 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40690 | 40690 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
40691 | 40692 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
40693 | 40694 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40695 | 40695 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
40696 | 40696 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
40697 | 40697 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
40698 | 40698 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
40699 | 40699 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40700 | 40700 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
40701 | 40701 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
40702 | 40702 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
40703 | 40703 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
40704 | 40704 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
40705 | 40705 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40706 | 40706 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40707 | 40707 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40708 | 40708 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40709 | 40709 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40710 | 40710 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
40711 | 40711 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40712 | 40712 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40713 | 40713 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
40714 | 40714 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
40715 | 40715 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40716 | 40716 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40717 | 40717 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40718 | 40718 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
40719 | 40719 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40720 | 40721 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40722 | 40723 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40724 | 40724 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40725 | 40725 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40726 | 40726 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
40727 | 40727 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
40728 | 40728 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
40729 | 40729 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40730 | 40730 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
40731 | 40731 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40732 | 40732 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40733 | 40733 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40734 | 40734 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40735 | 40736 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40737 | 40737 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40738 | 40738 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40739 | 40739 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40740 | 40740 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40741 | 40741 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40742 | 40742 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40743 | 40743 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40744 | 40744 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40745 | 40745 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40746 | 40746 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
40747 | 40747 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40748 | 40748 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
40749 | 40749 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40750 | 40750 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40751 | 40751 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40752 | 40752 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40753 | 40754 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40755 | 40755 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40756 | 40756 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40757 | 40757 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40758 | 40758 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40759 | 40759 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40760 | 40760 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40761 | 40761 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40762 | 40762 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40763 | 40763 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40764 | 40764 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
40765 | 40765 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40766 | 40766 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
40767 | 40767 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40768 | 40768 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40769 | 40769 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40770 | 40770 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40771 | 40772 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40773 | 40773 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40774 | 40774 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40775 | 40775 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40776 | 40776 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40777 | 40777 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40778 | 40778 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40779 | 40779 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40780 | 40780 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40781 | 40781 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40782 | 40782 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
40783 | 40783 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40784 | 40784 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
40785 | 40785 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40786 | 40786 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40787 | 40787 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40788 | 40788 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40789 | 40790 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40791 | 40791 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40792 | 40792 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40793 | 40793 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40794 | 40794 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40795 | 40795 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40796 | 40796 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40797 | 40797 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40798 | 40798 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40799 | 40799 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40800 | 40800 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
40801 | 40801 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
40802 | 40802 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40803 | 40803 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40804 | 40804 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40805 | 40805 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
40806 | 40806 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40807 | 40808 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40809 | 40810 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40811 | 40811 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40812 | 40812 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40813 | 40813 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
40814 | 40814 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
40815 | 40815 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40816 | 40816 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40817 | 40818 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40819 | 40819 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40820 | 40820 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40821 | 40821 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40822 | 40822 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40823 | 40823 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40824 | 40824 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40825 | 40825 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40826 | 40826 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40827 | 40827 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40828 | 40829 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40830 | 40830 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40831 | 40831 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40832 | 40832 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40833 | 40833 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40834 | 40834 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40835 | 40835 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40836 | 40836 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40837 | 40837 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40838 | 40838 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40839 | 40840 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40841 | 40841 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40842 | 40842 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40843 | 40843 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40844 | 40844 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40845 | 40845 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40846 | 40846 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40847 | 40847 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40848 | 40848 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40849 | 40849 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40850 | 40851 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40852 | 40852 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40853 | 40853 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40854 | 40854 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40855 | 40855 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40856 | 40856 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40857 | 40857 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40858 | 40858 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40859 | 40859 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
40860 | 40860 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
40861 | 40861 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40862 | 40862 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40863 | 40863 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40864 | 40864 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40865 | 40865 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40866 | 40866 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40867 | 40867 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40868 | 40868 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40869 | 40869 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40870 | 40870 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40871 | 40872 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40873 | 40873 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40874 | 40875 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40876 | 40876 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40877 | 40878 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40879 | 40879 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40880 | 40881 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40882 | 40882 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40883 | 40884 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40885 | 40885 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40886 | 40886 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40887 | 40888 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40889 | 40889 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40890 | 40891 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40892 | 40892 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40893 | 40894 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40895 | 40895 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40896 | 40897 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40898 | 40898 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40899 | 40900 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40901 | 40901 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40902 | 40902 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40903 | 40904 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40905 | 40905 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40906 | 40907 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40908 | 40908 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40909 | 40910 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40911 | 40911 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40912 | 40913 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40914 | 40914 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40915 | 40916 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40917 | 40917 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40918 | 40918 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40919 | 40919 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40920 | 40921 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40922 | 40922 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40923 | 40924 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40925 | 40925 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40926 | 40927 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40928 | 40928 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40929 | 40930 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40931 | 40931 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40932 | 40933 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40934 | 40934 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40935 | 40935 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40936 | 40937 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40938 | 40938 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40939 | 40940 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40941 | 40941 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40942 | 40943 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40944 | 40944 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40945 | 40946 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40947 | 40947 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40948 | 40949 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40950 | 40950 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40951 | 40951 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40952 | 40953 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40954 | 40954 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40955 | 40956 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40957 | 40957 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40958 | 40959 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40960 | 40960 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40961 | 40962 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40963 | 40963 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40964 | 40965 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40966 | 40966 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40967 | 40967 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40968 | 40968 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40969 | 40970 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40971 | 40971 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40972 | 40973 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40974 | 40974 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40975 | 40976 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40977 | 40977 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40978 | 40979 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40980 | 40980 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40981 | 40982 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40983 | 40983 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40984 | 40984 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40985 | 40986 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40987 | 40987 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40988 | 40989 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40990 | 40990 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40991 | 40992 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40993 | 40993 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40994 | 40995 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40996 | 40996 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40997 | 40998 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40999 | 40999 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41000 | 41000 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41001 | 41002 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41003 | 41003 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41004 | 41005 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41006 | 41006 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41007 | 41008 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41009 | 41009 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41010 | 41011 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41012 | 41012 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41013 | 41014 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41015 | 41015 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41016 | 41016 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41017 | 41017 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41018 | 41019 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41020 | 41020 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41021 | 41022 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41023 | 41023 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41024 | 41025 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41026 | 41026 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41027 | 41028 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41029 | 41029 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41030 | 41031 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41032 | 41032 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41033 | 41033 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41034 | 41035 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41036 | 41036 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41037 | 41038 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41039 | 41039 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41040 | 41041 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41042 | 41042 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41043 | 41044 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41045 | 41045 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41046 | 41047 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41048 | 41048 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41049 | 41049 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41050 | 41051 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41052 | 41052 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41053 | 41054 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41055 | 41055 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41056 | 41057 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41058 | 41058 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41059 | 41060 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41061 | 41061 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41062 | 41063 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41064 | 41064 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
41065 | 41065 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
41066 | 41066 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41067 | 41067 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41068 | 41068 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41069 | 41069 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41070 | 41070 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41071 | 41071 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
41072 | 41072 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41073 | 41073 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41074 | 41074 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41075 | 41075 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41076 | 41077 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41078 | 41078 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41079 | 41080 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41081 | 41081 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41082 | 41083 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41084 | 41084 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41085 | 41086 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41087 | 41087 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41088 | 41089 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41090 | 41090 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41091 | 41091 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41092 | 41093 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41094 | 41094 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41095 | 41096 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41097 | 41097 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41098 | 41099 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41100 | 41100 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41101 | 41102 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41103 | 41103 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41104 | 41105 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41106 | 41106 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41107 | 41107 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41108 | 41109 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41110 | 41110 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41111 | 41112 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41113 | 41113 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41114 | 41115 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41116 | 41116 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41117 | 41118 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41119 | 41119 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41120 | 41121 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41122 | 41122 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41123 | 41123 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41124 | 41124 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41125 | 41126 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41127 | 41127 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41128 | 41129 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41130 | 41130 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41131 | 41132 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41133 | 41133 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41134 | 41135 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41136 | 41136 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41137 | 41138 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41139 | 41139 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41140 | 41140 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41141 | 41142 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41143 | 41143 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41144 | 41145 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41146 | 41146 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41147 | 41148 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41149 | 41149 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41150 | 41151 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41152 | 41152 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41153 | 41154 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41155 | 41155 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41156 | 41156 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41157 | 41158 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41159 | 41159 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41160 | 41161 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41162 | 41162 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41163 | 41164 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41165 | 41165 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41166 | 41167 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41168 | 41168 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41169 | 41170 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41171 | 41171 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41172 | 41172 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41173 | 41173 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41174 | 41175 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41176 | 41176 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41177 | 41178 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41179 | 41179 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41180 | 41181 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41182 | 41182 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41183 | 41184 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41185 | 41185 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41186 | 41187 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41188 | 41188 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41189 | 41189 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41190 | 41191 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41192 | 41192 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41193 | 41194 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41195 | 41195 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41196 | 41197 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41198 | 41198 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41199 | 41200 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41201 | 41201 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41202 | 41203 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41204 | 41204 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41205 | 41205 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41206 | 41207 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41208 | 41208 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41209 | 41210 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41211 | 41211 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41212 | 41213 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41214 | 41214 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41215 | 41216 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41217 | 41217 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41218 | 41219 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41220 | 41220 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41221 | 41221 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41222 | 41222 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41223 | 41224 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41225 | 41225 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41226 | 41227 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41228 | 41228 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41229 | 41230 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41231 | 41231 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41232 | 41233 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41234 | 41234 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41235 | 41236 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41237 | 41237 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41238 | 41238 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41239 | 41240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41241 | 41241 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41242 | 41243 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41244 | 41244 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41245 | 41246 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41247 | 41247 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41248 | 41249 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41250 | 41250 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41251 | 41252 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41253 | 41253 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41254 | 41254 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41255 | 41256 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41257 | 41257 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41258 | 41259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41260 | 41260 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41261 | 41262 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41263 | 41263 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41264 | 41265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41266 | 41266 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41267 | 41268 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41269 | 41269 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
41270 | 41270 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
41271 | 41271 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41272 | 41272 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41273 | 41273 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41274 | 41274 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41275 | 41275 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41276 | 41276 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41277 | 41277 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41278 | 41278 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41279 | 41279 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41280 | 41281 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41282 | 41283 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41284 | 41285 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41286 | 41287 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41288 | 41289 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41290 | 41291 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41292 | 41293 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41294 | 41295 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41296 | 41297 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41298 | 41299 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41300 | 41300 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41301 | 41302 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41303 | 41304 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41305 | 41306 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41307 | 41308 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41309 | 41310 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41311 | 41312 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41313 | 41314 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41315 | 41316 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41317 | 41318 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41319 | 41320 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41321 | 41321 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41322 | 41323 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41324 | 41325 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41326 | 41327 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41328 | 41329 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41330 | 41331 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41332 | 41333 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41334 | 41335 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41336 | 41337 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41338 | 41339 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41340 | 41341 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41342 | 41342 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41343 | 41343 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41344 | 41345 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41346 | 41347 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41348 | 41349 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41350 | 41351 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41352 | 41353 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41354 | 41355 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41356 | 41357 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41358 | 41359 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41360 | 41361 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41362 | 41363 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41364 | 41364 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41365 | 41366 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41367 | 41368 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41369 | 41370 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41371 | 41372 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41373 | 41374 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41375 | 41376 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41377 | 41378 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41379 | 41380 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41381 | 41382 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41383 | 41384 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41385 | 41385 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41386 | 41387 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41388 | 41389 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41390 | 41391 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41392 | 41393 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41394 | 41395 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41396 | 41397 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41398 | 41399 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41400 | 41401 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41402 | 41403 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41404 | 41405 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41406 | 41406 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41407 | 41407 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41408 | 41409 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41410 | 41411 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41412 | 41413 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41414 | 41415 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41416 | 41417 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41418 | 41419 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41420 | 41421 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41422 | 41423 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41424 | 41425 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41426 | 41427 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41428 | 41428 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41429 | 41430 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41431 | 41432 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41433 | 41434 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41435 | 41436 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41437 | 41438 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41439 | 41440 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41441 | 41442 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41443 | 41444 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41445 | 41446 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41447 | 41448 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41449 | 41449 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41450 | 41451 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41452 | 41453 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41454 | 41455 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41456 | 41457 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41458 | 41459 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41460 | 41461 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41462 | 41463 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41464 | 41465 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41466 | 41467 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41468 | 41469 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41470 | 41470 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41471 | 41471 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41472 | 41473 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41474 | 41475 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41476 | 41477 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41478 | 41479 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41480 | 41481 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41482 | 41483 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41484 | 41485 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41486 | 41487 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41488 | 41489 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41490 | 41491 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41492 | 41492 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41493 | 41494 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41495 | 41496 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41497 | 41498 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41499 | 41500 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41501 | 41502 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41503 | 41504 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41505 | 41506 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41507 | 41508 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41509 | 41510 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41511 | 41512 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41513 | 41513 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41514 | 41515 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41516 | 41517 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41518 | 41519 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41520 | 41521 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41522 | 41523 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41524 | 41525 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41526 | 41527 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41528 | 41529 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41530 | 41531 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41532 | 41533 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41534 | 41534 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
41535 | 41535 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
41536 | 41536 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41537 | 41537 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41538 | 41538 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41539 | 41539 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41540 | 41540 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41541 | 41541 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41542 | 41542 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41543 | 41543 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41544 | 41544 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41545 | 41546 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41547 | 41548 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41549 | 41550 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41551 | 41552 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41553 | 41554 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41555 | 41556 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41557 | 41558 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41559 | 41560 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41561 | 41562 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41563 | 41564 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41565 | 41565 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41566 | 41567 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41568 | 41569 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41570 | 41571 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41572 | 41573 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41574 | 41575 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41576 | 41577 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41578 | 41579 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41580 | 41581 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41582 | 41583 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41584 | 41585 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41586 | 41586 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41587 | 41588 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41589 | 41590 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41591 | 41592 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41593 | 41594 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41595 | 41596 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41597 | 41598 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41599 | 41600 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41601 | 41602 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41603 | 41604 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41605 | 41606 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41607 | 41607 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41608 | 41608 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41609 | 41610 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41611 | 41612 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41613 | 41614 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41615 | 41616 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41617 | 41618 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41619 | 41620 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41621 | 41622 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41623 | 41624 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41625 | 41626 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41627 | 41628 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41629 | 41629 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41630 | 41631 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41632 | 41633 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41634 | 41635 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41636 | 41637 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41638 | 41639 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41640 | 41641 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41642 | 41643 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41644 | 41645 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41646 | 41647 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41648 | 41649 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41650 | 41650 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41651 | 41652 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41653 | 41654 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41655 | 41656 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41657 | 41658 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41659 | 41660 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41661 | 41662 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41663 | 41664 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41665 | 41666 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41667 | 41668 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41669 | 41670 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41671 | 41671 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41672 | 41672 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41673 | 41674 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41675 | 41676 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41677 | 41678 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41679 | 41680 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41681 | 41682 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41683 | 41684 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41685 | 41686 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41687 | 41688 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41689 | 41690 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41691 | 41692 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41693 | 41693 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41694 | 41695 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41696 | 41697 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41698 | 41699 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41700 | 41701 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41702 | 41703 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41704 | 41705 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41706 | 41707 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41708 | 41709 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41710 | 41711 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41712 | 41713 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41714 | 41714 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41715 | 41716 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41717 | 41718 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41719 | 41720 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41721 | 41722 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41723 | 41724 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41725 | 41726 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41727 | 41728 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41729 | 41730 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41731 | 41732 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41733 | 41734 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41735 | 41735 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41736 | 41736 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41737 | 41738 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41739 | 41740 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41741 | 41742 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41743 | 41744 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41745 | 41746 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41747 | 41748 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41749 | 41750 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41751 | 41752 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41753 | 41754 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41755 | 41756 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41757 | 41757 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41758 | 41759 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41760 | 41761 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41762 | 41763 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41764 | 41765 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41766 | 41767 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41768 | 41769 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41770 | 41771 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41772 | 41773 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41774 | 41775 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41776 | 41777 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41778 | 41778 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41779 | 41780 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41781 | 41782 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41783 | 41784 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41785 | 41786 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41787 | 41788 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41789 | 41790 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41791 | 41792 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41793 | 41794 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41795 | 41796 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41797 | 41798 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41799 | 41799 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
41800 | 41800 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
41801 | 41801 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41802 | 41802 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
41803 | 41803 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41804 | 41804 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
41805 | 41806 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41807 | 41808 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41809 | 41809 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
41810 | 41810 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
41811 | 41811 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
41812 | 41812 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
41813 | 41814 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41815 | 41816 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41817 | 41817 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41818 | 41818 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41819 | 41820 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41821 | 41821 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41822 | 41822 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
41823 | 41824 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41825 | 41826 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41827 | 41827 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41828 | 41828 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41829 | 41830 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41831 | 41831 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41832 | 41832 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41833 | 41834 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41835 | 41836 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41837 | 41837 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41838 | 41838 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41839 | 41840 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41841 | 41841 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41842 | 41842 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41843 | 41844 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41845 | 41846 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41847 | 41847 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41848 | 41848 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41849 | 41850 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41851 | 41851 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41852 | 41852 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41853 | 41853 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
41854 | 41854 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
41855 | 41855 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41856 | 41856 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
41857 | 41857 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41858 | 41858 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
41859 | 41859 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
41860 | 41861 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41862 | 41863 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41864 | 41864 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
41865 | 41865 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
41866 | 41866 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
41867 | 41867 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
41868 | 41868 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41869 | 41869 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
41870 | 41870 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41871 | 41871 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41872 | 41872 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41873 | 41873 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41874 | 41874 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41875 | 41875 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41876 | 41876 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41877 | 41877 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41878 | 41878 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41879 | 41879 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41880 | 41880 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41881 | 41881 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41882 | 41882 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41883 | 41883 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
41884 | 41884 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41885 | 41885 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
41886 | 41886 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41887 | 41887 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41888 | 41888 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41889 | 41889 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41890 | 41890 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41891 | 41891 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41892 | 41892 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41893 | 41893 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41894 | 41894 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41895 | 41895 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41896 | 41896 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41897 | 41897 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41898 | 41898 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41899 | 41899 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
41900 | 41900 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41901 | 41901 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
41902 | 41902 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41903 | 41903 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41904 | 41904 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41905 | 41905 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41906 | 41906 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41907 | 41907 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41908 | 41908 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41909 | 41909 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41910 | 41910 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41911 | 41911 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41912 | 41912 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41913 | 41913 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41914 | 41914 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41915 | 41915 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
41916 | 41916 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41917 | 41917 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
41918 | 41918 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41919 | 41919 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41920 | 41920 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41921 | 41921 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41922 | 41922 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41923 | 41923 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41924 | 41924 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41925 | 41925 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41926 | 41926 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41927 | 41927 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41928 | 41928 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41929 | 41929 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41930 | 41930 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41931 | 41931 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
41932 | 41932 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
41933 | 41933 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
41934 | 41934 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
41935 | 41935 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
41936 | 41936 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
41937 | 41937 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
41938 | 41938 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
41939 | 41939 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41940 | 41940 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
41941 | 41941 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 25.0 Verto 27.0 Verto 29.9 Verto 30.0 Verto 33.3 Verto 15.0 208-240 Verto 18.0 208-240 Verto 19.0 208-240 Verto 27.0 480 Verto 30.0 480 Verto 36.0 480
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (113)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (113) | uint16 |  |  | 113
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (113) | uint16 | Registers |  | 60
3 | 4 | 2 | R | 0x03 | A | AC Current | float32 | A
5 | 6 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
7 | 8 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A
9 | 10 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A
11 | 12 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V
13 | 14 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V
15 | 16 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V
17 | 18 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
19 | 20 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V
21 | 22 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V
23 | 24 | 2 | R | 0x03 | W | AC Power | float32 | W
25 | 26 | 2 | R | 0x03 | Hz | Line Frequency | float32 | Hz
27 | 28 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
29 | 30 | 2 | R | 0x03 | VAr | AC Reactive Power | float32 | var
31 | 32 | 2 | R | 0x03 | PF | AC Power Factor | float32 | Pct
33 | 34 | 2 | R | 0x03 | WH | AC Energy | float32 | Wh
35 | 36 | 2 | R | 0x03 | DCA | DC Current | float32 | A |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
37 | 38 | 2 | R | 0x03 | DCV | DC Voltage | float32 | V |  | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
39 | 40 | 2 | R | 0x03 | DCW | DC Power | float32 | W
41 | 42 | 2 | R | 0x03 | TmpCab | Cabinet Temperature | float32 | C
43 | 44 | 2 | R | 0x03 | TmpSnk | Heat Sink Temperature | float32 | C |  | not supported
45 | 46 | 2 | R | 0x03 | TmpTrns | Transformer Temperature | float32 | C |  | not supported
47 | 48 | 2 | R | 0x03 | TmpOt | Other Temperature | float32 | C |  | not supported
49 | 49 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
50 | 50 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
51 | 52 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
53 | 54 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
55 | 56 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
57 | 58 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
59 | 60 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
61 | 62 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 82 (PV_STOR)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | from 0 to 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | from -1.0 to 0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 128
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers + 2 * number of battery inputs 4 MPPT and 1 BATTERY => 6 repeating blocks
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
31 | 31 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40 | 40 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
41 | 41 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
42 | 42 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
43 | 44 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
45 | 46 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
47 | 47 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
48 | 48 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
49 | 50 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
51 | 51 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
52 | 59 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
60 | 60 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
61 | 61 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
62 | 62 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
63 | 64 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
65 | 66 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
67 | 67 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
68 | 68 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
69 | 70 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
71 | 71 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
72 | 79 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'MPPT 4'
80 | 80 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF
81 | 81 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF
82 | 82 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF
83 | 84 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
85 | 86 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
87 | 87 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
88 | 88 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
89 | 90 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported
91 | 91 | 1 | R | 0x03 | module/5/ID | Input ID | uint16 |  |  | 5
92 | 99 | 8 | R | 0x03 | module/5/IDStr | Input ID Sting | string |  |  | 'StCha 5'
100 | 100 | 1 | R | 0x03 | module/5/DCA | DC Current | uint16 | A | DCA_SF | When the battery is discharged the data-points of the charge input are set to 0
101 | 101 | 1 | R | 0x03 | module/5/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
102 | 102 | 1 | R | 0x03 | module/5/DCW | DC Power | uint16 | W | DCW_SF | When the battery is discharged the data-points of the charge input are set to 0
103 | 104 | 2 | R | 0x03 | module/5/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Charge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
105 | 106 | 2 | R | 0x03 | module/5/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
107 | 107 | 1 | R | 0x03 | module/5/Tmp | Temperature | int16 | C |  | not supported
108 | 108 | 1 | R | 0x03 | module/5/DCSt | Operating State | enum16 |  |  | not supported
109 | 110 | 2 | R | 0x03 | module/5/DCEvt | Module Events | bitfield32 |  |  | not supported
111 | 111 | 1 | R | 0x03 | module/6/ID | Input ID | uint16 |  |  | 6
112 | 119 | 8 | R | 0x03 | module/6/IDStr | Input ID Sting | string |  |  | 'StDisCha 6'
120 | 120 | 1 | R | 0x03 | module/6/DCA | DC Current | uint16 | A | DCA_SF | When the battery is charged the data-points of the discharge input are set to 0
121 | 121 | 1 | R | 0x03 | module/6/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
122 | 122 | 1 | R | 0x03 | module/6/DCW | DC Power | uint16 | W | DCW_SF | When the battery is charged the data-points of the discharge input are set to 0
123 | 124 | 2 | R | 0x03 | module/6/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Discharge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
125 | 126 | 2 | R | 0x03 | module/6/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
127 | 127 | 1 | R | 0x03 | module/6/Tmp | Temperature | int16 | C |  | not supported
128 | 128 | 1 | R | 0x03 | module/6/DCSt | Operating State | enum16 |  |  | not supported
129 | 130 | 2 | R | 0x03 | module/6/DCEvt | Module Events | bitfield32 |  |  | not supported

## storage (124)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model storage (124) | uint16 |  |  | 124
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model storage (124) | uint16 | Registers |  | 24
3 | 3 | 1 | R | 0x03 | WChaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. The inverter is not fully capable of transferring power as reported by this reference value. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only | uint16 | W | WChaMax_SF
4 | 4 | 1 | R | 0x03 | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
5 | 5 | 1 | R | 0x03 | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
6 | 6 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
7 | 7 | 1 | R | 0x03 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF | not supported
8 | 8 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
9 | 9 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
10 | 10 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | not supported
11 | 11 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | not supported
12 | 12 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and WChaMax defines max. Discharge rate. See WChaMax for details | int16 | % WDisChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
14 | 14 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and WChaMax defines max. Charge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
15 | 15 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | not supported
16 | 16 | 1 | RW | 0x03 0x06 0x10 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | 0 - 28800
17 | 17 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | not supported
18 | 18 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet |  | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
19 | 19 | 1 | R | 0x03 | WChaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
20 | 20 | 1 | R | 0x03 | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
21 | 21 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
23 | 23 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
24 | 24 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | not supported
25 | 25 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2

## DERMeasureAC (701)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
3 | 3 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
4 | 4 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
5 | 5 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
6 | 6 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
7 | 8 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
9 | 10 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
11 | 11 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
12 | 12 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
13 | 13 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
14 | 14 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
15 | 15 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
16 | 16 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
17 | 17 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
18 | 19 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
20 | 23 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
24 | 27 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
28 | 31 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
32 | 35 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
39 | 39 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40 | 40 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
41 | 41 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
42 | 42 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
43 | 43 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
44 | 44 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
45 | 45 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
46 | 46 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
47 | 47 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
48 | 48 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
49 | 52 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
53 | 56 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
57 | 60 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
61 | 64 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
65 | 65 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
66 | 66 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
67 | 67 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
68 | 68 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
69 | 69 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
70 | 70 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
71 | 71 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
72 | 75 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
76 | 79 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
80 | 83 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
84 | 87 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
88 | 88 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
89 | 89 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
90 | 90 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
91 | 91 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
92 | 92 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
93 | 93 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
94 | 94 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
95 | 98 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
99 | 102 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
103 | 106 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
107 | 110 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
111 | 111 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
112 | 113 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
114 | 114 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
115 | 115 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
116 | 116 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
117 | 117 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
118 | 118 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
119 | 119 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
120 | 120 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
121 | 121 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
122 | 122 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
123 | 123 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
124 | 155 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported

## DERCapacity (702)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
4 | 4 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
5 | 5 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
6 | 6 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
7 | 7 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
8 | 8 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
9 | 9 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
10 | 10 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
11 | 11 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
12 | 12 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
13 | 13 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
14 | 14 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
15 | 15 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
16 | 16 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
17 | 17 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
19 | 19 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
20 | 20 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
21 | 21 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
22 | 22 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
23 | 23 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
24 | 25 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
26 | 26 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
27 | 27 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
28 | 28 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
29 | 29 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
30 | 30 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
31 | 31 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
32 | 32 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
33 | 33 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
34 | 34 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
35 | 35 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
36 | 36 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
37 | 37 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
38 | 38 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
39 | 39 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40 | 40 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
41 | 41 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
42 | 42 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
43 | 43 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
44 | 44 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
45 | 45 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
46 | 46 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
47 | 47 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
48 | 48 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
49 | 49 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
50 | 50 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
51 | 51 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
52 | 52 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6

## DEREnterService (703)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
3 | 3 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
5 | 5 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
6 | 7 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
8 | 9 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
10 | 11 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
12 | 13 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
14 | 15 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
18 | 18 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2

## DERCtlAC (704)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
3 | 3 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
5 | 6 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
7 | 8 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
9 | 9 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
10 | 10 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
11 | 12 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
13 | 14 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
15 | 15 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
17 | 17 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
18 | 18 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
19 | 20 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
21 | 22 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
23 | 23 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
24 | 24 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
25 | 26 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
27 | 28 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
29 | 29 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
30 | 30 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
31 | 31 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
32 | 33 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
34 | 35 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
36 | 36 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
37 | 37 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
38 | 38 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
39 | 40 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
41 | 42 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
43 | 43 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
46 | 47 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
48 | 49 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
50 | 50 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
51 | 51 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
52 | 52 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
53 | 53 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
54 | 54 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
55 | 55 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
56 | 56 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
57 | 57 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
58 | 58 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
59 | 59 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
60 | 60 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
62 | 62 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
64 | 64 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
65 | 65 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
66 | 66 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
67 | 67 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported

## DERVoltVar (705)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
23 | 24 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
59 | 60 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
66 | 66 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
77 | 78 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
79 | 79 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
80 | 80 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
81 | 81 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
82 | 82 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
83 | 83 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
84 | 84 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
85 | 85 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
86 | 86 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
87 | 87 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERVoltWatt (706)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
29 | 30 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40 | 41 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%

## DERTripLV (707)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHV (708)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripLF (709)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHF (710)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERFreqDroop (711)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
7 | 8 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
9 | 10 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
11 | 11 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
12 | 12 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
13 | 13 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
14 | 14 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
15 | 16 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
17 | 18 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
21 | 22 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
24 | 24 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
27 | 28 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
31 | 32 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
34 | 34 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
35 | 36 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
37 | 38 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
44 | 44 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
45 | 46 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
47 | 48 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
54 | 54 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)

## DERWattVar (712)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
18 | 18 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
34 | 34 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41 | 41 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
50 | 50 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
66 | 66 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
77 | 77 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
78 | 78 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERStorageCapacity (713)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
3 | 3 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
4 | 4 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
5 | 5 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
6 | 6 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
7 | 7 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
8 | 8 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
9 | 9 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0