## Complete Map
Fronius Verto Inverter Register Map with 3 MPPT and Integer+SF Inverter Model for US use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 10.0 Verto 12.5 Verto 15.0 Verto 17.5 Verto 20.0 Verto 22.0 Verto 24.0 Verto 10.0 208-240 Verto 12.0 208-240 Verto 10.0 480 Verto 12.5 480 Verto 15.0 480 Verto 20.0 480 Verto 24.0 480
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (103) | uint16 |  |  | 103
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (103) | uint16 | Registers |  | 50
40072 | 40072 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF
40075 | 40075 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF
40076 | 40076 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
40077 | 40077 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF
40078 | 40078 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF
40079 | 40079 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF
40080 | 40080 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
40081 | 40081 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF
40082 | 40082 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF
40083 | 40083 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
40084 | 40084 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
40085 | 40085 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
40086 | 40086 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
40088 | 40088 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
40089 | 40089 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
40090 | 40090 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
40091 | 40091 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
40092 | 40092 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
40093 | 40093 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
40094 | 40095 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
40096 | 40096 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
40097 | 40097 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40098 | 40098 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | not supported
40099 | 40099 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40100 | 40100 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | not supported
40101 | 40101 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
40102 | 40102 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
40103 | 40103 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
40104 | 40104 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
40105 | 40105 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
40106 | 40106 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
40107 | 40107 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
40108 | 40108 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40109 | 40109 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40110 | 40111 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40112 | 40113 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40114 | 40115 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40116 | 40117 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40118 | 40119 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40120 | 40121 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40122 | 40122 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40123 | 40123 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40124 | 40124 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
40125 | 40125 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40126 | 40126 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40127 | 40127 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40128 | 40128 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40129 | 40129 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40130 | 40130 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
40131 | 40131 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
40132 | 40132 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40133 | 40133 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40134 | 40134 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40135 | 40135 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40136 | 40136 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40137 | 40137 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
40138 | 40138 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
40139 | 40139 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40140 | 40140 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40141 | 40141 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
40142 | 40142 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
40143 | 40143 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40144 | 40144 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40145 | 40145 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
40146 | 40146 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
40147 | 40147 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
40148 | 40148 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
40149 | 40149 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40150 | 40150 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40151 | 40151 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40152 | 40152 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40153 | 40153 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40154 | 40154 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40155 | 40155 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40156 | 40156 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40157 | 40157 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40158 | 40158 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40159 | 40159 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40160 | 40160 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40161 | 40161 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40162 | 40162 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40163 | 40163 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40164 | 40164 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40165 | 40165 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40166 | 40166 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40167 | 40167 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40168 | 40168 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40169 | 40169 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40170 | 40170 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40171 | 40171 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40172 | 40172 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40173 | 40173 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40174 | 40174 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40175 | 40175 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40176 | 40176 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40177 | 40177 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40178 | 40178 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40180 | 40180 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40181 | 40181 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40182 | 40182 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40183 | 40183 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40184 | 40184 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40185 | 40185 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40186 | 40186 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40187 | 40190 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40191 | 40194 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40195 | 40198 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40199 | 40202 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40203 | 40206 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40207 | 40210 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40211 | 40211 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40212 | 40212 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40213 | 40213 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40214 | 40214 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40215 | 40216 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40217 | 40218 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40219 | 40222 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40223 | 40224 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40225 | 40225 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40226 | 40226 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40227 | 40227 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40228 | 40228 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40229 | 40229 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40230 | 40230 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40231 | 40231 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40232 | 40232 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40233 | 40233 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40234 | 40234 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40235 | 40235 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40236 | 40236 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40237 | 40237 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40238 | 40238 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40239 | 40239 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40243 | 40243 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40245 | 40245 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40249 | 40249 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40251 | 40251 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40252 | 40252 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40253 | 40253 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40254 | 40254 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40255 | 40255 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 68
40256 | 40256 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40257 | 40257 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40258 | 40258 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40259 | 40259 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40260 | 40261 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40262 | 40262 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 3 MPPT => 3 repeating block
40263 | 40263 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40264 | 40264 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40265 | 40272 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40273 | 40273 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40274 | 40274 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40275 | 40275 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40276 | 40277 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40278 | 40279 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40280 | 40280 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40281 | 40281 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40282 | 40283 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
40284 | 40284 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
40285 | 40292 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40293 | 40293 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
40294 | 40294 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
40295 | 40295 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
40296 | 40297 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40298 | 40299 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40300 | 40300 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
40301 | 40301 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
40302 | 40303 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
40304 | 40304 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
40305 | 40312 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
40313 | 40313 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
40314 | 40314 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
40315 | 40315 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
40316 | 40317 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40318 | 40319 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40320 | 40320 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
40321 | 40321 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
40322 | 40323 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40324 | 40324 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
40325 | 40325 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
40326 | 40326 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
40327 | 40327 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
40328 | 40328 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
40329 | 40329 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
40330 | 40331 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
40332 | 40333 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
40334 | 40334 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
40335 | 40335 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
40336 | 40336 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
40337 | 40337 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
40338 | 40338 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
40339 | 40339 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
40340 | 40340 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
40341 | 40342 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
40343 | 40346 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
40347 | 40350 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
40351 | 40354 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
40355 | 40358 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
40359 | 40359 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
40360 | 40360 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
40361 | 40361 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
40362 | 40362 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40363 | 40363 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
40364 | 40364 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
40365 | 40365 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
40366 | 40366 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
40367 | 40367 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
40368 | 40368 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
40369 | 40369 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
40370 | 40370 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
40371 | 40371 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
40372 | 40375 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
40376 | 40379 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
40380 | 40383 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
40384 | 40387 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
40388 | 40388 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
40389 | 40389 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
40390 | 40390 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
40391 | 40391 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
40392 | 40392 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
40393 | 40393 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
40394 | 40394 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
40395 | 40398 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
40399 | 40402 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
40403 | 40406 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
40407 | 40410 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
40411 | 40411 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
40412 | 40412 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
40413 | 40413 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
40414 | 40414 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
40415 | 40415 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
40416 | 40416 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
40417 | 40417 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
40418 | 40421 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
40422 | 40425 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
40426 | 40429 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
40430 | 40433 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
40434 | 40434 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
40435 | 40436 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
40437 | 40437 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40438 | 40438 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40439 | 40439 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
40440 | 40440 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40441 | 40441 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
40442 | 40442 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
40443 | 40443 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40444 | 40444 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
40445 | 40445 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
40446 | 40446 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
40447 | 40478 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40479 | 40479 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
40480 | 40480 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
40481 | 40481 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
40482 | 40482 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
40483 | 40483 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40484 | 40484 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
40485 | 40485 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
40486 | 40486 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
40487 | 40487 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
40488 | 40488 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
40489 | 40489 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40490 | 40490 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
40491 | 40491 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
40492 | 40492 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
40493 | 40493 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
40494 | 40494 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
40495 | 40495 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
40496 | 40496 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
40497 | 40497 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
40498 | 40498 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
40499 | 40499 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
40500 | 40500 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
40501 | 40501 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
40502 | 40503 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
40504 | 40504 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
40505 | 40505 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
40506 | 40506 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
40507 | 40507 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
40508 | 40508 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
40509 | 40509 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
40510 | 40510 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
40511 | 40511 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
40512 | 40512 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
40513 | 40513 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
40514 | 40514 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
40515 | 40515 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
40516 | 40516 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
40517 | 40517 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40518 | 40518 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
40519 | 40519 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
40520 | 40520 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
40521 | 40521 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
40522 | 40522 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
40523 | 40523 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
40524 | 40524 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
40525 | 40525 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40526 | 40526 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
40527 | 40527 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
40528 | 40528 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
40529 | 40529 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
40530 | 40530 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40531 | 40531 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
40532 | 40532 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
40533 | 40533 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
40534 | 40534 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
40535 | 40535 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40536 | 40537 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40538 | 40539 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
40540 | 40541 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
40542 | 40543 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
40544 | 40545 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
40546 | 40547 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
40548 | 40548 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
40549 | 40549 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40550 | 40550 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
40551 | 40551 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
40552 | 40552 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
40553 | 40553 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40554 | 40555 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40556 | 40557 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
40558 | 40558 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
40559 | 40559 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
40560 | 40561 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
40562 | 40563 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
40564 | 40564 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
40565 | 40565 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40566 | 40566 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
40567 | 40567 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
40568 | 40569 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
40570 | 40571 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40572 | 40572 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
40573 | 40573 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
40574 | 40575 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
40576 | 40577 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
40578 | 40578 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40579 | 40579 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
40580 | 40580 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
40581 | 40582 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
40583 | 40584 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
40585 | 40585 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
40586 | 40586 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
40587 | 40587 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
40588 | 40589 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40590 | 40591 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
40592 | 40592 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40593 | 40593 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
40594 | 40594 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
40595 | 40596 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
40597 | 40598 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
40599 | 40599 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
40600 | 40600 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
40601 | 40601 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
40602 | 40602 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
40603 | 40603 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
40604 | 40604 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
40605 | 40605 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
40606 | 40606 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
40607 | 40607 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
40608 | 40608 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
40609 | 40609 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40610 | 40610 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40611 | 40611 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
40612 | 40612 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
40613 | 40613 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40614 | 40614 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
40615 | 40615 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
40616 | 40616 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40617 | 40617 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
40618 | 40618 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
40619 | 40619 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40620 | 40620 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40621 | 40621 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40622 | 40622 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
40623 | 40623 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40624 | 40625 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40626 | 40627 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40628 | 40628 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40629 | 40629 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40630 | 40630 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
40631 | 40631 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
40632 | 40632 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
40633 | 40633 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40634 | 40634 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
40635 | 40635 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40636 | 40636 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40637 | 40637 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40638 | 40638 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40639 | 40640 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40641 | 40641 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40642 | 40642 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40643 | 40643 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40644 | 40644 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40645 | 40645 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40646 | 40646 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40647 | 40647 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40648 | 40648 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40649 | 40649 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40650 | 40650 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
40651 | 40651 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40652 | 40652 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
40653 | 40653 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40654 | 40654 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40655 | 40655 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40656 | 40656 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40657 | 40658 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40659 | 40659 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40660 | 40660 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40661 | 40661 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40662 | 40662 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40663 | 40663 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40664 | 40664 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40665 | 40665 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40666 | 40666 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40667 | 40667 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40668 | 40668 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
40669 | 40669 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40670 | 40670 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
40671 | 40671 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40672 | 40672 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40673 | 40673 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40674 | 40674 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40675 | 40676 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40677 | 40677 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40678 | 40678 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40679 | 40679 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40680 | 40680 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40681 | 40681 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40682 | 40682 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40683 | 40683 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40684 | 40684 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40685 | 40685 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40686 | 40686 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
40687 | 40687 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
40688 | 40688 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
40689 | 40689 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
40690 | 40690 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
40691 | 40691 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40692 | 40692 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
40693 | 40694 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
40695 | 40695 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40696 | 40696 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40697 | 40697 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40698 | 40698 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40699 | 40699 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40700 | 40700 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40701 | 40701 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
40702 | 40702 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
40703 | 40703 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40704 | 40704 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
40705 | 40705 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
40706 | 40706 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40707 | 40707 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40708 | 40708 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40709 | 40709 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
40710 | 40710 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
40711 | 40712 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
40713 | 40714 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
40715 | 40715 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
40716 | 40716 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40717 | 40717 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
40718 | 40718 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
40719 | 40719 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40720 | 40720 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40721 | 40722 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40723 | 40723 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40724 | 40724 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40725 | 40725 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40726 | 40726 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40727 | 40727 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40728 | 40728 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40729 | 40729 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40730 | 40730 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40731 | 40731 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40732 | 40733 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40734 | 40734 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40735 | 40735 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40736 | 40736 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40737 | 40737 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40738 | 40738 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40739 | 40739 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40740 | 40740 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40741 | 40741 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40742 | 40742 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40743 | 40744 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40745 | 40745 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40746 | 40746 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40747 | 40747 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40748 | 40748 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40749 | 40749 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40750 | 40750 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40751 | 40751 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40752 | 40752 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
40753 | 40753 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40754 | 40755 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
40756 | 40756 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40757 | 40757 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
40758 | 40758 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
40759 | 40759 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40760 | 40760 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
40761 | 40761 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
40762 | 40762 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40763 | 40763 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
40764 | 40764 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
40765 | 40765 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40766 | 40766 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40767 | 40767 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40768 | 40768 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40769 | 40769 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40770 | 40770 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40771 | 40771 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40772 | 40772 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40773 | 40773 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40774 | 40774 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40775 | 40776 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40777 | 40777 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40778 | 40779 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40780 | 40780 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40781 | 40782 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40783 | 40783 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40784 | 40785 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40786 | 40786 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40787 | 40788 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40789 | 40789 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40790 | 40790 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40791 | 40792 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40793 | 40793 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40794 | 40795 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40796 | 40796 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40797 | 40798 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40799 | 40799 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40800 | 40801 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40802 | 40802 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40803 | 40804 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40805 | 40805 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40806 | 40806 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40807 | 40808 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40809 | 40809 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40810 | 40811 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40812 | 40812 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40813 | 40814 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40815 | 40815 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40816 | 40817 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40818 | 40818 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40819 | 40820 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40821 | 40821 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40822 | 40822 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40823 | 40823 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40824 | 40825 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40826 | 40826 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40827 | 40828 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40829 | 40829 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40830 | 40831 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40832 | 40832 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40833 | 40834 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40835 | 40835 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40836 | 40837 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40838 | 40838 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40839 | 40839 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40840 | 40841 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40842 | 40842 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40843 | 40844 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40845 | 40845 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40846 | 40847 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40848 | 40848 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40849 | 40850 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40851 | 40851 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40852 | 40853 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40854 | 40854 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40855 | 40855 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40856 | 40857 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40858 | 40858 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40859 | 40860 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40861 | 40861 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40862 | 40863 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40864 | 40864 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40865 | 40866 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40867 | 40867 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40868 | 40869 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40870 | 40870 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40871 | 40871 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40872 | 40872 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40873 | 40874 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40875 | 40875 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40876 | 40877 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40878 | 40878 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40879 | 40880 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40881 | 40881 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40882 | 40883 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40884 | 40884 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40885 | 40886 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40887 | 40887 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40888 | 40888 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40889 | 40890 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40891 | 40891 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40892 | 40893 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40894 | 40894 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40895 | 40896 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40897 | 40897 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40898 | 40899 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40900 | 40900 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40901 | 40902 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40903 | 40903 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40904 | 40904 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40905 | 40906 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40907 | 40907 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40908 | 40909 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40910 | 40910 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40911 | 40912 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40913 | 40913 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40914 | 40915 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40916 | 40916 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40917 | 40918 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40919 | 40919 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
40920 | 40920 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40921 | 40921 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40922 | 40923 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40924 | 40924 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40925 | 40926 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40927 | 40927 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40928 | 40929 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40930 | 40930 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40931 | 40932 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40933 | 40933 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40934 | 40935 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40936 | 40936 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40937 | 40937 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40938 | 40939 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40940 | 40940 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40941 | 40942 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40943 | 40943 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40944 | 40945 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40946 | 40946 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40947 | 40948 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40949 | 40949 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40950 | 40951 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40952 | 40952 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
40953 | 40953 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40954 | 40955 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40956 | 40956 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40957 | 40958 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40959 | 40959 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40960 | 40961 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40962 | 40962 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40963 | 40964 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40965 | 40965 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40966 | 40967 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40968 | 40968 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
40969 | 40969 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
40970 | 40970 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
40971 | 40971 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
40972 | 40972 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
40973 | 40973 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
40974 | 40974 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
40975 | 40975 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
40976 | 40976 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
40977 | 40977 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
40978 | 40978 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
40979 | 40979 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40980 | 40981 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40982 | 40982 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40983 | 40984 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40985 | 40985 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40986 | 40987 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40988 | 40988 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40989 | 40990 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40991 | 40991 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
40992 | 40993 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
40994 | 40994 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
40995 | 40995 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40996 | 40997 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40998 | 40998 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
40999 | 41000 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41001 | 41001 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41002 | 41003 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41004 | 41004 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41005 | 41006 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41007 | 41007 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41008 | 41009 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41010 | 41010 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41011 | 41011 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41012 | 41013 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41014 | 41014 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41015 | 41016 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41017 | 41017 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41018 | 41019 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41020 | 41020 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41021 | 41022 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41023 | 41023 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41024 | 41025 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41026 | 41026 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41027 | 41027 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41028 | 41028 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41029 | 41030 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41031 | 41031 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41032 | 41033 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41034 | 41034 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41035 | 41036 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41037 | 41037 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41038 | 41039 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41040 | 41040 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41041 | 41042 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41043 | 41043 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41044 | 41044 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41045 | 41046 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41047 | 41047 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41048 | 41049 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41050 | 41050 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41051 | 41052 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41053 | 41053 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41054 | 41055 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41056 | 41056 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41057 | 41058 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41059 | 41059 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41060 | 41060 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41061 | 41062 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41063 | 41063 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41064 | 41065 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41066 | 41066 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41067 | 41068 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41069 | 41069 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41070 | 41071 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41072 | 41072 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41073 | 41074 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41075 | 41075 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41076 | 41076 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41077 | 41077 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41078 | 41079 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41080 | 41080 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41081 | 41082 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41083 | 41083 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41084 | 41085 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41086 | 41086 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41087 | 41088 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41089 | 41089 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41090 | 41091 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41092 | 41092 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41093 | 41093 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41094 | 41095 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41096 | 41096 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41097 | 41098 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41099 | 41099 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41100 | 41101 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41102 | 41102 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41103 | 41104 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41105 | 41105 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41106 | 41107 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41108 | 41108 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41109 | 41109 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41110 | 41111 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41112 | 41112 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41113 | 41114 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41115 | 41115 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41116 | 41117 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41118 | 41118 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41119 | 41120 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41121 | 41121 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41122 | 41123 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41124 | 41124 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41125 | 41125 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41126 | 41126 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41127 | 41128 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41129 | 41129 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41130 | 41131 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41132 | 41132 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41133 | 41134 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41135 | 41135 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41136 | 41137 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41138 | 41138 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
41139 | 41140 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41141 | 41141 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41142 | 41142 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41143 | 41144 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41145 | 41145 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41146 | 41147 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41148 | 41148 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41149 | 41150 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41151 | 41151 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41152 | 41153 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41154 | 41154 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41155 | 41156 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41157 | 41157 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41158 | 41158 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41159 | 41160 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41161 | 41161 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41162 | 41163 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41164 | 41164 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41165 | 41166 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41167 | 41167 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41168 | 41169 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41170 | 41170 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41171 | 41172 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41173 | 41173 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
41174 | 41174 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
41175 | 41175 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41176 | 41176 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41177 | 41177 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41178 | 41178 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41179 | 41179 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41180 | 41180 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41181 | 41181 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41182 | 41182 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41183 | 41183 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41184 | 41185 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41186 | 41187 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41188 | 41189 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41190 | 41191 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41192 | 41193 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41194 | 41195 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41196 | 41197 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41198 | 41199 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41200 | 41201 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41202 | 41203 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41204 | 41204 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41205 | 41206 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41207 | 41208 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41209 | 41210 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41211 | 41212 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41213 | 41214 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41215 | 41216 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41217 | 41218 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41219 | 41220 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41221 | 41222 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41223 | 41224 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41225 | 41225 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41226 | 41227 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41228 | 41229 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41230 | 41231 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41232 | 41233 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41234 | 41235 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41236 | 41237 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41238 | 41239 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41240 | 41241 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41242 | 41243 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41244 | 41245 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41246 | 41246 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41247 | 41247 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41248 | 41249 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41250 | 41251 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41252 | 41253 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41254 | 41255 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41256 | 41257 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41258 | 41259 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41260 | 41261 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41262 | 41263 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41264 | 41265 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41266 | 41267 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41268 | 41268 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41269 | 41270 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41271 | 41272 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41273 | 41274 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41275 | 41276 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41277 | 41278 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41279 | 41280 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41281 | 41282 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41283 | 41284 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41285 | 41286 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41287 | 41288 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41289 | 41289 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41290 | 41291 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41292 | 41293 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41294 | 41295 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41296 | 41297 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41298 | 41299 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41300 | 41301 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41302 | 41303 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41304 | 41305 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41306 | 41307 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41308 | 41309 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41310 | 41310 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41311 | 41311 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41312 | 41313 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41314 | 41315 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41316 | 41317 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41318 | 41319 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41320 | 41321 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41322 | 41323 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41324 | 41325 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41326 | 41327 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41328 | 41329 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41330 | 41331 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41332 | 41332 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41333 | 41334 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41335 | 41336 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41337 | 41338 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41339 | 41340 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41341 | 41342 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41343 | 41344 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41345 | 41346 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41347 | 41348 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41349 | 41350 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41351 | 41352 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41353 | 41353 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41354 | 41355 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41356 | 41357 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41358 | 41359 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41360 | 41361 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41362 | 41363 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41364 | 41365 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41366 | 41367 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41368 | 41369 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41370 | 41371 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41372 | 41373 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41374 | 41374 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41375 | 41375 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41376 | 41377 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41378 | 41379 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41380 | 41381 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41382 | 41383 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41384 | 41385 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41386 | 41387 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41388 | 41389 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41390 | 41391 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41392 | 41393 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41394 | 41395 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41396 | 41396 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41397 | 41398 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41399 | 41400 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41401 | 41402 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41403 | 41404 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41405 | 41406 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41407 | 41408 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41409 | 41410 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41411 | 41412 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41413 | 41414 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41415 | 41416 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41417 | 41417 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41418 | 41419 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41420 | 41421 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41422 | 41423 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41424 | 41425 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41426 | 41427 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41428 | 41429 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41430 | 41431 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41432 | 41433 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41434 | 41435 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41436 | 41437 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41438 | 41438 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
41439 | 41439 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
41440 | 41440 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41441 | 41441 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
41442 | 41442 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41443 | 41443 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
41444 | 41444 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
41445 | 41445 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
41446 | 41446 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
41447 | 41447 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41448 | 41448 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41449 | 41450 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41451 | 41452 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41453 | 41454 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41455 | 41456 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41457 | 41458 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41459 | 41460 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41461 | 41462 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41463 | 41464 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41465 | 41466 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41467 | 41468 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41469 | 41469 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41470 | 41471 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41472 | 41473 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41474 | 41475 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41476 | 41477 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41478 | 41479 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41480 | 41481 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41482 | 41483 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41484 | 41485 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41486 | 41487 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41488 | 41489 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41490 | 41490 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41491 | 41492 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41493 | 41494 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41495 | 41496 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41497 | 41498 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41499 | 41500 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41501 | 41502 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41503 | 41504 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41505 | 41506 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41507 | 41508 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41509 | 41510 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41511 | 41511 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41512 | 41512 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41513 | 41514 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41515 | 41516 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41517 | 41518 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41519 | 41520 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41521 | 41522 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41523 | 41524 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41525 | 41526 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41527 | 41528 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41529 | 41530 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41531 | 41532 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41533 | 41533 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41534 | 41535 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41536 | 41537 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41538 | 41539 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41540 | 41541 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41542 | 41543 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41544 | 41545 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41546 | 41547 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41548 | 41549 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41550 | 41551 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41552 | 41553 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41554 | 41554 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41555 | 41556 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41557 | 41558 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41559 | 41560 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41561 | 41562 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41563 | 41564 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41565 | 41566 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41567 | 41568 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41569 | 41570 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41571 | 41572 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41573 | 41574 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41575 | 41575 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41576 | 41576 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41577 | 41578 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41579 | 41580 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41581 | 41582 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41583 | 41584 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41585 | 41586 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41587 | 41588 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41589 | 41590 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41591 | 41592 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41593 | 41594 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41595 | 41596 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41597 | 41597 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41598 | 41599 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41600 | 41601 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41602 | 41603 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41604 | 41605 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41606 | 41607 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41608 | 41609 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41610 | 41611 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41612 | 41613 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41614 | 41615 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41616 | 41617 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41618 | 41618 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41619 | 41620 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41621 | 41622 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41623 | 41624 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41625 | 41626 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41627 | 41628 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41629 | 41630 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41631 | 41632 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41633 | 41634 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41635 | 41636 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41637 | 41638 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41639 | 41639 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41640 | 41640 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
41641 | 41642 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41643 | 41644 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41645 | 41646 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41647 | 41648 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41649 | 41650 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41651 | 41652 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41653 | 41654 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41655 | 41656 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41657 | 41658 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
41659 | 41660 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
41661 | 41661 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
41662 | 41663 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41664 | 41665 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41666 | 41667 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41668 | 41669 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41670 | 41671 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41672 | 41673 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41674 | 41675 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41676 | 41677 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41678 | 41679 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41680 | 41681 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41682 | 41682 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
41683 | 41684 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41685 | 41686 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41687 | 41688 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41689 | 41690 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41691 | 41692 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41693 | 41694 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41695 | 41696 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41697 | 41698 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41699 | 41700 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
41701 | 41702 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41703 | 41703 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
41704 | 41704 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
41705 | 41705 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41706 | 41706 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
41707 | 41707 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41708 | 41708 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
41709 | 41710 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41711 | 41712 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41713 | 41713 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
41714 | 41714 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
41715 | 41715 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
41716 | 41716 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
41717 | 41718 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41719 | 41720 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41721 | 41721 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41722 | 41722 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41723 | 41724 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41725 | 41725 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41726 | 41726 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
41727 | 41728 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41729 | 41730 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41731 | 41731 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41732 | 41732 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41733 | 41734 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41735 | 41735 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41736 | 41736 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41737 | 41738 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41739 | 41740 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41741 | 41741 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41742 | 41742 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41743 | 41744 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41745 | 41745 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41746 | 41746 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
41747 | 41748 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
41749 | 41750 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
41751 | 41751 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41752 | 41752 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41753 | 41754 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
41755 | 41755 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
41756 | 41756 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41757 | 41757 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
41758 | 41758 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
41759 | 41759 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
41760 | 41760 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
41761 | 41761 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
41762 | 41762 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
41763 | 41763 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
41764 | 41765 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
41766 | 41767 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
41768 | 41768 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
41769 | 41769 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
41770 | 41770 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
41771 | 41771 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
41772 | 41772 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41773 | 41773 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
41774 | 41774 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
41775 | 41775 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41776 | 41776 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41777 | 41777 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41778 | 41778 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41779 | 41779 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41780 | 41780 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41781 | 41781 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41782 | 41782 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41783 | 41783 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41784 | 41784 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41785 | 41785 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41786 | 41786 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41787 | 41787 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
41788 | 41788 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41789 | 41789 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
41790 | 41790 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41791 | 41791 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41792 | 41792 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41793 | 41793 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41794 | 41794 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41795 | 41795 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41796 | 41796 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41797 | 41797 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41798 | 41798 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41799 | 41799 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41800 | 41800 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41801 | 41801 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41802 | 41802 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41803 | 41803 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
41804 | 41804 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41805 | 41805 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
41806 | 41806 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41807 | 41807 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41808 | 41808 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41809 | 41809 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41810 | 41810 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41811 | 41811 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41812 | 41812 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41813 | 41813 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41814 | 41814 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41815 | 41815 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41816 | 41816 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41817 | 41817 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41818 | 41818 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41819 | 41819 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
41820 | 41820 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
41821 | 41821 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
41822 | 41822 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
41823 | 41823 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41824 | 41824 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41825 | 41825 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41826 | 41826 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41827 | 41827 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
41828 | 41828 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41829 | 41829 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41830 | 41830 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41831 | 41831 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41832 | 41832 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41833 | 41833 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
41834 | 41834 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41835 | 41835 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
41836 | 41836 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
41837 | 41837 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
41838 | 41838 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
41839 | 41839 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
41840 | 41840 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
41841 | 41841 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
41842 | 41842 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
41843 | 41843 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
41844 | 41844 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
41845 | 41845 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Verto 10.0 Verto 12.5 Verto 15.0 Verto 17.5 Verto 20.0 Verto 22.0 Verto 24.0 Verto 10.0 208-240 Verto 12.0 208-240 Verto 10.0 480 Verto 12.5 480 Verto 15.0 480 Verto 20.0 480 Verto 24.0 480
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (103)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (103) | uint16 |  |  | 103
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (103) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF
6 | 6 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF
7 | 7 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
8 | 8 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF
9 | 9 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF
10 | 10 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF
11 | 11 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
12 | 12 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF
13 | 13 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF
14 | 14 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
15 | 15 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
16 | 16 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
17 | 17 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
20 | 20 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
21 | 21 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
22 | 22 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
23 | 23 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
24 | 24 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
25 | 26 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
27 | 27 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
28 | 28 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
29 | 29 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
31 | 31 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
33 | 33 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
34 | 34 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
35 | 35 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
39 | 39 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40 | 40 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
41 | 42 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
43 | 44 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
45 | 46 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
47 | 48 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
49 | 50 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
51 | 52 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4 (PV)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | 0.0
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | 0.0
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | 1.0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF | not supported
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF | not supported
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF | not supported
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | not supported
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 68
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | number of mppt trackers 3 MPPT => 3 repeating block
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
31 | 31 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40 | 40 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
41 | 41 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
42 | 42 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
43 | 44 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
45 | 46 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
47 | 47 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
48 | 48 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
49 | 50 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
51 | 51 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
52 | 59 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'MPPT 3'
60 | 60 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF
61 | 61 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF
62 | 62 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF
63 | 64 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
65 | 66 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
67 | 67 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
68 | 68 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
69 | 70 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported

## DERMeasureAC (701)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERMeasureAC (701) | uint16 |  |  | 701
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERMeasureAC (701) | uint16 | Registers |  | 153
3 | 3 | 1 | R | 0x03 | ACType | AC wiring type. | enum16 |  |  | 0: Single Phase 1: Split Phase
4 | 4 | 1 | R | 0x03 | St | Operating state of the DER. | enum16 |  |  | 0: Off 1: On
5 | 5 | 1 | R | 0x03 | InvSt | Enumerated value. Inverter state. | enum16 |  |  | 0: Off 1: Sleeping 2: Starting 3: Running 4: Throttled 5: Shutting Down 6: Fault 7: Standby
6 | 6 | 1 | R | 0x03 | ConnSt | Grid connection state of the DER. | enum16 |  |  | 0: Disconnected 1: Connected
7 | 8 | 2 | R | 0x03 | Alrm | Active alarms for the DER. | bitfield32 |  |  | Bit 0: Ground Fault Bit 2: AC Disconnect Open Bit 4: Grid Disconnect Bit 8: Frequency Above Limit Bit 9: Frequency Under Limit Bit 10: AC Voltage Above Limit Bit 11: AC Voltage Under Limit Bit 15: Hardware Test Failure Bit 16: Manufacturer Alarm
9 | 10 | 2 | R | 0x03 | DERMode | Current operational characteristics of the DER. | bitfield32 |  |  | not supported
11 | 11 | 1 | R | 0x03 | W | Total active power. Active power is positive for DER generation and negative for absorption. | int16 | W | W_SF
12 | 12 | 1 | R | 0x03 | VA | Total apparent power. | int16 | VA | VA_SF | not supported
13 | 13 | 1 | R | 0x03 | Var | Total reactive power. | int16 | Var | Var_SF
14 | 14 | 1 | R | 0x03 | PF | Power factor. The sign of power factor should be the sign of active power. | int16 |  | PF_SF | not supported
15 | 15 | 1 | R | 0x03 | A | Total AC current. | int16 | A | A_SF | not supported
16 | 16 | 1 | R | 0x03 | LLV | Line to line AC voltage as an average of active phases. | uint16 | V | V_SF
17 | 17 | 1 | R | 0x03 | LNV | Line to neutral AC voltage as an average of active phases. | uint16 | V | V_SF
18 | 19 | 2 | R | 0x03 | Hz | AC frequency. | uint32 | Hz | Hz_SF
20 | 23 | 4 | R | 0x03 | TotWhInj | Total active energy injected (Quadrants 1 & 4). | uint64 | Wh | TotWh_SF | not supported
24 | 27 | 4 | R | 0x03 | TotWhAbs | Total active energy absorbed (Quadrants 2 & 3). | uint64 | Wh | TotWh_SF | not supported
28 | 31 | 4 | R | 0x03 | TotVarhInj | Total reactive energy injected (Quadrants 1 & 2). | uint64 | Varh | TotVarh_SF | not supported
32 | 35 | 4 | R | 0x03 | TotVarhAbs | Total reactive energy absorbed (Quadrants 3 & 4). | uint64 | Varh | TotVarh_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpAmb | Ambient temperature. | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpCab | Cabinet temperature. | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | TmpSnk | Heat sink temperature. | int16 | C | Tmp_SF | not supported
39 | 39 | 1 | R | 0x03 | TmpTrns | Transformer temperature. | int16 | C | Tmp_SF | not supported
40 | 40 | 1 | R | 0x03 | TmpSw | IGBT/MOSFET temperature. | int16 | C | Tmp_SF | not supported
41 | 41 | 1 | R | 0x03 | TmpOt | Other temperature. | int16 | C | Tmp_SF | not supported
42 | 42 | 1 | R | 0x03 | WL1 | Active power L1. | int16 | W | W_SF | not supported
43 | 43 | 1 | R | 0x03 | VAL1 | Apparent power L1. | int16 | VA | VA_SF | not supported
44 | 44 | 1 | R | 0x03 | VarL1 | Reactive power L1. | int16 | Var | Var_SF | not supported
45 | 45 | 1 | R | 0x03 | PFL1 | Power factor phase L1. | int16 |  | PF_SF | not supported
46 | 46 | 1 | R | 0x03 | AL1 | Current phase L1. | int16 | A | A_SF | not supported
47 | 47 | 1 | R | 0x03 | VL1L2 | Phase voltage L1-L2. | uint16 | V | V_SF
48 | 48 | 1 | R | 0x03 | VL1 | Phase voltage L1-N. | uint16 | V | V_SF
49 | 52 | 4 | R | 0x03 | TotWhInjL1 | Total active energy injected L1. | uint64 | Wh | TotWh_SF | not supported
53 | 56 | 4 | R | 0x03 | TotWhAbsL1 | Total active energy absorbed L1. | uint64 | Wh | TotWh_SF | not supported
57 | 60 | 4 | R | 0x03 | TotVarhInjL1 | Total reactive energy injected L1. | uint64 | Varh | TotVarh_SF | not supported
61 | 64 | 4 | R | 0x03 | TotVarhAbsL1 | Total reactive energy absorbed L1. | uint64 | Varh | TotVarh_SF | not supported
65 | 65 | 1 | R | 0x03 | WL2 | Active power L2. | int16 | W | W_SF | not supported
66 | 66 | 1 | R | 0x03 | VAL2 | Apparent power L2. | int16 | VA | VA_SF | not supported
67 | 67 | 1 | R | 0x03 | VarL2 | Reactive power L2. | int16 | Var | Var_SF | not supported
68 | 68 | 1 | R | 0x03 | PFL2 | Power factor L2. | int16 |  | PF_SF | not supported
69 | 69 | 1 | R | 0x03 | AL2 | Current L2. | int16 | A | A_SF | not supported
70 | 70 | 1 | R | 0x03 | VL2L3 | Phase voltage L2-L3. | uint16 | V | V_SF | not supported
71 | 71 | 1 | R | 0x03 | VL2 | Phase voltage L2-N. | uint16 | V | V_SF
72 | 75 | 4 | R | 0x03 | TotWhInjL2 | Total active energy injected L2. | uint64 | Wh | TotWh_SF | not supported
76 | 79 | 4 | R | 0x03 | TotWhAbsL2 | Total active energy absorbed L2. | uint64 | Wh | TotWh_SF | not supported
80 | 83 | 4 | R | 0x03 | TotVarhInjL2 | Total reactive energy injected L2. | uint64 | Varh | TotVarh_SF | not supported
84 | 87 | 4 | R | 0x03 | TotVarhAbsL2 | Total reactive energy absorbed L2. | uint64 | Varh | TotVarh_SF | not supported
88 | 88 | 1 | R | 0x03 | WL3 | Active power L3. | int16 | W | W_SF | not supported
89 | 89 | 1 | R | 0x03 | VAL3 | Apparent power L3. | int16 | VA | VA_SF | not supported
90 | 90 | 1 | R | 0x03 | VarL3 | Reactive power L3. | int16 | Var | Var_SF | not supported
91 | 91 | 1 | R | 0x03 | PFL3 | Power factor L3. | int16 |  | PF_SF | not supported
92 | 92 | 1 | R | 0x03 | AL3 | Current L3. | int16 | A | A_SF | not supported
93 | 93 | 1 | R | 0x03 | VL3L1 | Phase voltage L3-L1. | uint16 | V | V_SF | not supported
94 | 94 | 1 | R | 0x03 | VL3 | Phase voltage L3-N. | uint16 | V | V_SF | not supported
95 | 98 | 4 | R | 0x03 | TotWhInjL3 | Total active energy injected L3. | uint64 | Wh | TotWh_SF | not supported
99 | 102 | 4 | R | 0x03 | TotWhAbsL3 | Total active energy absorbed L3. | uint64 | Wh | TotWh_SF | not supported
103 | 106 | 4 | R | 0x03 | TotVarhInjL3 | Total reactive energy injected L3. | uint64 | Varh | TotVarh_SF | not supported
107 | 110 | 4 | R | 0x03 | TotVarhAbsL3 | Total reactive energy absorbed L3. | uint64 | Varh | TotVarh_SF | not supported
111 | 111 | 1 | R | 0x03 | ThrotPct | Throttling in pct of maximum active power. | uint16 | Pct |  | not supported
112 | 113 | 2 | R | 0x03 | ThrotSrc | Active throttling source. | bitfield32 |  |  | not supported
114 | 114 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
115 | 115 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
116 | 116 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2
117 | 117 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
118 | 118 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | not supported
119 | 119 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | not supported
120 | 120 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
121 | 121 | 1 | R | 0x03 | TotWh_SF | Active energy scale factor. | sunssf |  |  | not supported
122 | 122 | 1 | R | 0x03 | TotVarh_SF | Reactive energy scale factor. | sunssf |  |  | not supported
123 | 123 | 1 | R | 0x03 | Tmp_SF | Temperature scale factor. | sunssf |  |  | not supported
124 | 155 | 32 | R | 0x03 | MnAlrmInfo | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. | string |  |  | not supported

## DERCapacity (702)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCapacity (702) | uint16 |  |  | 702
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCapacity (702) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | WMaxRtg | Maximum active power rating at unity power factor in watts. | uint16 | W | W_SF
4 | 4 | 1 | R | 0x03 | WOvrExtRtg | Active power rating at specified over-excited power factor in watts. | uint16 | W | W_SF
5 | 5 | 1 | R | 0x03 | WOvrExtRtgPF | Specified over-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
6 | 6 | 1 | R | 0x03 | WUndExtRtg | Active power rating at specified under-excited power factor in watts. | uint16 | W | W_SF
7 | 7 | 1 | R | 0x03 | WUndExtRtgPF | Specified under-excited power factor. | uint16 |  | PF_SF | 0 to 1.0
8 | 8 | 1 | R | 0x03 | VAMaxRtg | Maximum apparent power rating in voltamperes. | uint16 | VA | VA_SF
9 | 9 | 1 | R | 0x03 | VarMaxInjRtg | Maximum injected reactive power rating in vars. | uint16 | Var | Var_SF
10 | 10 | 1 | R | 0x03 | VarMaxAbsRtg | Maximum absorbed reactive power rating in vars. | uint16 | Var | Var_SF
11 | 11 | 1 | R | 0x03 | WChaRteMaxRtg | Maximum active power charge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
12 | 12 | 1 | R | 0x03 | WDisChaRteMaxRtg | Maximum active power discharge rate in watts. | uint16 | W | W_SF | Battery Available: based on configured battery No Battery Available: 0
13 | 13 | 1 | R | 0x03 | VAChaRteMaxRtg | Maximum apparent power charge rate in voltamperes. | uint16 | VA | VA_SF | Battery Available: based on configured battery No Battery Available: 0
14 | 14 | 1 | R | 0x03 | VADisChaRteMaxRtg | Maximum apparent power discharge rate in voltamperes. | uint16 | VA | VA_SF | not supported
15 | 15 | 1 | R | 0x03 | VNomRtg | AC voltage nominal rating. | uint16 | V | V_SF | 208.0 * *Actual range may vary based on inverter configuration or country setup
16 | 16 | 1 | R | 0x03 | VMaxRtg | AC voltage maximum rating. | uint16 | V | V_SF | 228.8 * *Actual range may vary based on inverter configuration or country setup
17 | 17 | 1 | R | 0x03 | VMinRtg | AC voltage minimum rating. | uint16 | V | V_SF | 183.0 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | R | 0x03 | AMaxRtg | AC current maximum rating in amps. | uint16 | A | A_SF | not supported
19 | 19 | 1 | R | 0x03 | PFOvrExtRtg | Power factor over-excited rating. | uint16 |  | PF_SF | not supported
20 | 20 | 1 | R | 0x03 | PFUndExtRtg | Power factor under-excited rating. | uint16 |  | PF_SF | not supported
21 | 21 | 1 | R | 0x03 | ReactSusceptRtg | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. | uint16 | S | S_SF | 6kW: 0.000058 10kW: 0.001830
22 | 22 | 1 | R | 0x03 | NorOpCatRtg | Normal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 1 (Category B)
23 | 23 | 1 | R | 0x03 | AbnOpCatRtg | Abnormal operating performance category as specified in IEEE 1547-2018. | enum16 |  |  | 2 (Category III)
24 | 25 | 2 | R | 0x03 | CtrlModes | Supported control mode functions. | bitfield32 |  |  | Bit 0: Limit Maximum Active Power Bit 1: Fixed Active Power Bit 2: Fixed Reactive Power Bit 3: Fixed Power Factor Bit 4: Volt Var Function Bit 5: Freq Watt Function Bit 6: Dynamic Reactive Current Function Bit 7: Low Voltage Trip Bit 8: High Voltage Trip Bit 9: Watt Var Function Bit 10: Volt Watt Function Bit 12: Low Frequency Trip Bit 13: High Frequency Trip
26 | 26 | 1 | R | 0x03 | IntIslandCatRtg | Intentional island categories. | bitfield16 |  |  | not supported
27 | 27 | 1 | R | 0x03 | WMax | Maximum active power setting used to adjust maximum active power setting. | uint16 | W | W_SF | not supported
28 | 28 | 1 | R | 0x03 | WMaxOvrExt | Active power setting at specified over-excited power factor in watts. | uint16 | W | W_SF | not supported
29 | 29 | 1 | R | 0x03 | WOvrExtPF | Specified over-excited power factor. | uint16 |  | PF_SF | not supported
30 | 30 | 1 | R | 0x03 | WMaxUndExt | Active power setting at specified under-excited power factor in watts. | uint16 | W | W_SF | not supported
31 | 31 | 1 | R | 0x03 | WUndExtPF | Specified under-excited power factor. | uint16 |  | PF_SF | not supported
32 | 32 | 1 | R | 0x03 | VAMax | Maximum apparent power setting used to adjust maximum apparent power rating. | uint16 | VA | VA_SF | not supported
33 | 33 | 1 | R | 0x03 | VarMaxInj | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. | uint16 | Var | Var_SF | not supported
34 | 34 | 1 | R | 0x03 | VarMaxAbs | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. | uint16 | Var | Var_SF | not supported
35 | 35 | 1 | R | 0x03 | WChaRteMax | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. | uint16 | W | W_SF | not supported
36 | 36 | 1 | R | 0x03 | WDisChaRteMax | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. | uint16 | W | W_SF | not supported
37 | 37 | 1 | R | 0x03 | VAChaRteMax | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. | uint16 | VA | VA_SF | not supported
38 | 38 | 1 | R | 0x03 | VADisChaRteMax | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. | uint16 | VA | VA_SF | not supported
39 | 39 | 1 | R | 0x03 | VNom | Nominal AC voltage setting. | uint16 | V | V_SF | not supported
40 | 40 | 1 | R | 0x03 | VMax | AC voltage maximum setting used to adjust AC voltage maximum rating. | uint16 | V | V_SF | not supported
41 | 41 | 1 | R | 0x03 | VMin | AC voltage minimum setting used to adjust AC voltage minimum rating. | uint16 | V | V_SF | not supported
42 | 42 | 1 | R | 0x03 | AMax | Maximum AC current setting used to adjust maximum AC current rating. | uint16 | A | A_SF | not supported
43 | 43 | 1 | R | 0x03 | PFOvrExt | Power factor over-excited setting. | uint16 |  | PF_SF | not supported
44 | 44 | 1 | R | 0x03 | PFUndExt | Power factor under-excited setting. | uint16 |  | PF_SF | not supported
45 | 45 | 1 | R | 0x03 | IntIslandCat | Intentional island categories. | bitfield16 |  |  | not supported
46 | 46 | 1 | R | 0x03 | W_SF | Active power scale factor. | sunssf |  |  | 0
47 | 47 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
48 | 48 | 1 | R | 0x03 | VA_SF | Apparent power scale factor. | sunssf |  |  | 0
49 | 49 | 1 | R | 0x03 | Var_SF | Reactive power scale factor. | sunssf |  |  | 0
50 | 50 | 1 | R | 0x03 | V_SF | Voltage scale factor. | sunssf |  |  | -2
51 | 51 | 1 | R | 0x03 | A_SF | Current scale factor. | sunssf |  |  | not supported
52 | 52 | 1 | R | 0x03 | S_SF | Susceptance scale factor. | sunssf |  |  | -6

## DEREnterService (703)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DEREnterService (703) | uint16 |  |  | 703
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DEREnterService (703) | uint16 | Registers |  | 17
3 | 3 | 1 | RW | 0x03 0x06 0x10 | ES | Permit enter service. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | ESVHi | Enter service voltage high threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51 % * *Actual range may vary based on inverter configuration or country setup
5 | 5 | 1 | RW | 0x03 0x06 0x10 | ESVLo | Enter service voltage low threshold as percent of normal voltage. | uint16 | Pct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
6 | 7 | 2 | RW | 0x03 0x06 0x10 | ESHzHi | Enter service frequency high threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
8 | 9 | 2 | RW | 0x03 0x06 0x10 | ESHzLo | Enter service frequency low threshold. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
10 | 11 | 2 | RW | 0x03 0x06 0x10 | ESDlyTms | Enter service delay time in seconds. | uint32 | Secs |  | 0 to 900 * *Actual range may vary based on inverter configuration or country setup
12 | 13 | 2 | R | 0x03 | ESRndTms | Enter service random delay in seconds. | uint32 | Secs |  | not supported
14 | 15 | 2 | RW | 0x03 0x06 0x10 | ESRmpTms | Enter service ramp time in seconds. | uint32 | Secs |  | 1 to 100000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | R | 0x03 | ESDlyRemTms | Enter service delay time remaining in seconds. | uint32 | Secs |  | not supported
18 | 18 | 1 | R | 0x03 | V_SF | Voltage percentage scale factor. | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | Hz_SF | Frequency scale factor. | sunssf |  |  | -2

## DERCtlAC (704)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERCtlAC (704) | uint16 |  |  | 704
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERCtlAC (704) | uint16 | Registers |  | 65
3 | 3 | 1 | RW | 0x03 0x06 0x10 | PFWInjEna | Power factor enable when injecting active power. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | PFWInjEnaRvrt | Power factor reversion timer when injecting active power enable. | enum16 |  |  | 0: Disabled 1: Enabled
5 | 6 | 2 | RW | 0x03 0x06 0x10 | PFWInjRvrtTms | Power factor reversion timer when injecting active power. | uint32 | Secs |  | 0 to 4294967294
7 | 8 | 2 | R | 0x03 | PFWInjRvrtRem | Power factor reversion time remaining when injecting active power. | uint32 | Secs |  | 0 to 4294967294
9 | 9 | 1 | R | 0x03 | PFWAbsEna | Power factor enable when absorbing active power. | enum16 |  |  | not supported
10 | 10 | 1 | R | 0x03 | PFWAbsEnaRvrt | Power factor reversion timer when absorbing active power enable. | enum16 |  |  | not supported
11 | 12 | 2 | R | 0x03 | PFWAbsRvrtTms | Power factor reversion timer when absorbing active power. | uint32 | Secs |  | not supported
13 | 14 | 2 | R | 0x03 | PFWAbsRvrtRem | Power factor reversion time remaining when absorbing active power. | uint32 | Secs |  | not supported
15 | 15 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEna | Limit maximum active power percent enable. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
17 | 17 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrt | Reversion limit maximum active power percent value. | uint16 | Pct | WMaxLimPct_SF | 0% to 100%
18 | 18 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPctEnaRvrt | Reversion limit maximum active power percent value enable. | enum16 |  |  | 0: Disabled 1: Enabled
19 | 20 | 2 | RW | 0x03 0x06 0x10 | WMaxLimPctRvrtTms | Limit maximum active power percent reversion time. | uint32 | Secs |  | 0 to 4294967294
21 | 22 | 2 | R | 0x03 | WMaxLimPctRvrtRem | Limit maximum active power percent reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
23 | 23 | 1 | R | 0x03 | WSetEna | Set active power enable. | enum16 |  |  | not supported
24 | 24 | 1 | R | 0x03 | WSetMod | Set active power mode. | enum16 |  |  | not supported
25 | 26 | 2 | R | 0x03 | WSet | Active power setting value in watts. | int32 | W | WSet_SF | not supported
27 | 28 | 2 | R | 0x03 | WSetRvrt | Reversion active power setting value in watts. | int32 | W | WSet_SF | not supported
29 | 29 | 1 | R | 0x03 | WSetPct | Active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
30 | 30 | 1 | R | 0x03 | WSetPctRvrt | Reversion active power setting value as percent. | int16 | Pct | WSetPct_SF | not supported
31 | 31 | 1 | R | 0x03 | WSetEnaRvrt | Reversion active power function enable. | enum16 |  |  | not supported
32 | 33 | 2 | R | 0x03 | WSetRvrtTms | Set active power reversion time. | uint32 | Secs |  | not supported
34 | 35 | 2 | R | 0x03 | WSetRvrtRem | Set active power reversion time remaining. | uint32 | Secs |  | not supported
36 | 36 | 1 | RW | 0x03 0x06 0x10 | VarSetEna | Set reactive power enable. | enum16 |  |  | 0: Disabled 1: Enabled
37 | 37 | 1 | RW | 0x03 0x06 0x10 | VarSetMod | Set reactive power mode. | enum16 |  |  | 0 to 3
38 | 38 | 1 | RW | 0x03 0x06 0x10 | VarSetPri | Reactive power priority. | enum16 |  |  | 1 (Reactive)
39 | 40 | 2 | R | 0x03 | VarSet | Reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
41 | 42 | 2 | R | 0x03 | VarSetRvrt | Reversion reactive power setting value in vars. | int32 | Var | VarSet_SF | not supported
43 | 43 | 1 | RW | 0x03 0x06 0x10 | VarSetPct | Reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | VarSetPctRvrt | Reversion reactive power setting value as percent. | int16 | Pct | VarSetPct_SF | -100% to 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | VarSetEnaRvrt | Reversion reactive power function enable. | enum16 |  |  | 0: Disabled 1: Enabled
46 | 47 | 2 | RW | 0x03 0x06 0x10 | VarSetRvrtTms | Set reactive power reversion time. | uint32 | Secs |  | 0 to 4294967294
48 | 49 | 2 | R | 0x03 | VarSetRvrtRem | Set reactive power reversion time remaining. | uint32 | Secs |  | 0 to 4294967294
50 | 50 | 1 | R | 0x03 | WRmp | Ramp rate for increases in active power during normal generation. | uint16 | %Max/Sec |  | not supported
51 | 51 | 1 | R | 0x03 | WRmpRef | Ramp rate reference unit for increases in active power or current during normal generation. | enum16 |  |  | not supported
52 | 52 | 1 | R | 0x03 | VarRmp | Ramp rate based on max reactive power per second. | uint16 | %Max/Sec |  | not supported
53 | 53 | 1 | R | 0x03 | AntiIslEna | Anti-islanding enable. | enum16 |  |  | not supported
54 | 54 | 1 | R | 0x03 | PF_SF | Power factor scale factor. | sunssf |  |  | -2
55 | 55 | 1 | R | 0x03 | WMaxLimPct_SF | Limit maximum power scale factor. | sunssf |  |  | -2
56 | 56 | 1 | R | 0x03 | WSet_SF | Active power scale factor. | sunssf |  |  | not supported
57 | 57 | 1 | R | 0x03 | WSetPct_SF | Active power pct scale factor. | sunssf |  |  | not supported
58 | 58 | 1 | R | 0x03 | VarSet_SF | Reactive power scale factor. | sunssf |  |  | not supported
59 | 59 | 1 | R | 0x03 | VarSetPct_SF | Reactive power pct scale factor. | sunssf |  |  | -2
60 | 60 | 1 | RW | 0x03 0x06 0x10 | PFWInj/PF | Power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | PFWInj/Ext | Power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
62 | 62 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/PF | Reversion power factor setpoint when injecting active power. | uint16 |  | PF_SF | 0.8 to 1 * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | PFWInjRvrt/Ext | Reversion power factor excitation setpoint when injecting active power. | enum16 |  |  | 0: Over Excited 1: Under Excited
64 | 64 | 1 | R | 0x03 | PFWAbs/PF | Power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
65 | 65 | 1 | R | 0x03 | PFWAbs/Ext | Power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported
66 | 66 | 1 | R | 0x03 | PFWAbsRvrt/PF | Reversion power factor setpoint when absorbing active power. | uint16 |  | PF_SF | not supported
67 | 67 | 1 | R | 0x03 | PFWAbsRvrt/Ext | Reversion power factor excitation setpoint when absorbing active power. | enum16 |  |  | not supported

## DERVoltVar (705)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltVar (705) | uint16 |  |  | 705
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltVar (705) | uint16 | Registers |  | 85
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 4
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -3
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 4
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
23 | 24 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 4
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | R | 0x03 | Crv/2/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 4
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | R | 0x03 | Crv/3/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
59 | 60 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
66 | 66 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 4
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRef | Vref adjustment as percentage of nominal voltage. | uint16 | VRefPct | V_SF | 95 to 105 * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | R | 0x03 | Crv/4/VRefAuto | Autonomous vref value as a percentage of nominal voltage. | uint16 | VRefPct | V_SF | not supported
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoEna | Enable autonomous vref. | enum16 |  |  | 0: Disabled 1: Enabled
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/VRefAutoTms | Autonomous vref time constant. | uint16 | Secs |  | 299 to 11500 * *Actual range may vary based on inverter configuration or country setup
77 | 78 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0.023 to 138 * *Actual range may vary based on inverter configuration or country setup
79 | 79 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
80 | 80 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
81 | 81 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
82 | 82 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
83 | 83 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
84 | 84 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
85 | 85 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
86 | 86 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 50% to 150% * *Actual range may vary based on inverter configuration or country setup
87 | 87 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | DeptRef | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERVoltWatt (706)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERVoltWatt (706) | uint16 |  |  | 706
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERVoltWatt (706) | uint16 | Registers |  | 57
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | Volt-Watt control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 3
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve watt points. | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -1
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 2 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 2 to 3
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0
29 | 30 | 2 | RW | 0x03 0x06 0x10 | Crv/2/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
34 | 34 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 2 to 3
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0
40 | 41 | 2 | RW | 0x03 0x06 0x10 | Crv/3/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 2 to 3
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Crv/4/RspTms | Open loop response time. | uint32 | Secs | RspTms_SF | 0 to 1380 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 100% to 149.51%
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | 100%
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51%
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Active power in percent of rated active power. | int16 | DeptRef | DeptRef_SF | -100% to 100%

## DERTripLV (707)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLV (707) | uint16 |  |  | 707
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLV (707) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHV (708)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHV (708) | uint16 |  |  | 708
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHV (708) | uint16 | Registers |  | 203
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high voltage trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | V_SF | Scale factor for curve voltage points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 12 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
13 | 14 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
18 | 18 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
19 | 20 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
28 | 28 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
29 | 30 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
31 | 31 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
32 | 33 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
34 | 34 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 37 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
38 | 39 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
40 | 40 | 1 | R | 0x03 | Crv/1/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
43 | 43 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
44 | 44 | 1 | R | 0x03 | Crv/1/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
47 | 47 | 1 | R | 0x03 | Crv/1/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
48 | 49 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
50 | 50 | 1 | R | 0x03 | Crv/1/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
56 | 56 | 1 | R | 0x03 | Crv/1/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
57 | 58 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
59 | 59 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
62 | 63 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
65 | 66 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
68 | 69 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
71 | 72 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
74 | 75 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
77 | 77 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
78 | 79 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
80 | 80 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
81 | 82 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
83 | 83 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
84 | 85 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
86 | 86 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
87 | 88 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
89 | 89 | 1 | R | 0x03 | Crv/2/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
90 | 91 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
92 | 92 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
93 | 93 | 1 | R | 0x03 | Crv/2/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
94 | 95 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
96 | 96 | 1 | R | 0x03 | Crv/2/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
99 | 99 | 1 | R | 0x03 | Crv/2/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
100 | 101 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
102 | 102 | 1 | R | 0x03 | Crv/2/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 105 | 1 | R | 0x03 | Crv/2/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
106 | 107 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
108 | 108 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
109 | 109 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
110 | 110 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
111 | 112 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
113 | 113 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
114 | 115 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
116 | 116 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
117 | 118 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
119 | 119 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
120 | 121 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
122 | 122 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
123 | 124 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
125 | 125 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
126 | 126 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
127 | 128 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
129 | 129 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
132 | 132 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
133 | 134 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
135 | 135 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
139 | 140 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
141 | 141 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
142 | 142 | 1 | R | 0x03 | Crv/3/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
143 | 144 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
145 | 145 | 1 | R | 0x03 | Crv/3/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
146 | 147 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
148 | 148 | 1 | R | 0x03 | Crv/3/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
149 | 150 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
151 | 151 | 1 | R | 0x03 | Crv/3/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
152 | 153 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
154 | 154 | 1 | R | 0x03 | Crv/3/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
155 | 156 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
157 | 157 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
158 | 158 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
159 | 159 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
160 | 161 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
162 | 162 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
163 | 164 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
165 | 165 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
166 | 167 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
168 | 168 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
169 | 170 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
171 | 171 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | 0% to 149.51% * *Actual range may vary based on inverter configuration or country setup
172 | 173 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
174 | 174 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
175 | 175 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
176 | 177 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
178 | 178 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
182 | 183 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
184 | 184 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
185 | 186 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
187 | 187 | 1 | R | 0x03 | Crv/4/MayTrip/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 190 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
191 | 191 | 1 | R | 0x03 | Crv/4/MomCess/Pt/1/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 194 | 1 | R | 0x03 | Crv/4/MomCess/Pt/2/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
195 | 196 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
197 | 197 | 1 | R | 0x03 | Crv/4/MomCess/Pt/3/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
200 | 200 | 1 | R | 0x03 | Crv/4/MomCess/Pt/4/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
201 | 202 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
203 | 203 | 1 | R | 0x03 | Crv/4/MomCess/Pt/5/V | Curve voltage point as percentage. | uint16 | VRefPct | V_SF | not supported
204 | 205 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripLF (709)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripLF (709) | uint16 |  |  | 709
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripLF (709) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER low frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERTripHF (710)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERTripHF (710) | uint16 |  |  | 710
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERTripHF (710) | uint16 | Registers |  | 263
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER high frequency trip control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Index of curve points to adopt. First curve index is 1. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last adopt curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 5
7 | 7 | 1 | R | 0x03 | NCrvSet | Number of stored curves supported. | uint16 |  |  | 4
8 | 8 | 1 | R | 0x03 | Hz_SF | Scale factor for curve frequency points. | sunssf |  |  | -2
9 | 9 | 1 | R | 0x03 | Tms_SF | Scale factor for curve time points. | sunssf |  |  | -2
10 | 10 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
11 | 11 | 1 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
12 | 13 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
14 | 15 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
16 | 17 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
18 | 19 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
20 | 21 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
22 | 23 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
24 | 25 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
26 | 27 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
28 | 29 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
30 | 31 | 2 | RW | 0x03 0x06 0x10 | Crv/1/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
32 | 32 | 1 | R | 0x03 | Crv/1/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
33 | 34 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
35 | 36 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
37 | 38 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
39 | 40 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
41 | 42 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
43 | 44 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
45 | 46 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
47 | 48 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
49 | 50 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
51 | 52 | 2 | R | 0x03 | Crv/1/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
53 | 53 | 1 | R | 0x03 | Crv/1/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
54 | 55 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
56 | 57 | 2 | R | 0x03 | Crv/1/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
58 | 59 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
60 | 61 | 2 | R | 0x03 | Crv/1/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
62 | 63 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
64 | 65 | 2 | R | 0x03 | Crv/1/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
66 | 67 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
68 | 69 | 2 | R | 0x03 | Crv/1/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
70 | 71 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
72 | 73 | 2 | R | 0x03 | Crv/1/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
74 | 74 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
76 | 77 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
78 | 79 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
80 | 81 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
82 | 83 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
84 | 85 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
86 | 87 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
88 | 89 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
90 | 91 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
92 | 93 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
94 | 95 | 2 | RW | 0x03 0x06 0x10 | Crv/2/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
96 | 96 | 1 | R | 0x03 | Crv/2/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
97 | 98 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
99 | 100 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
101 | 102 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
103 | 104 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
105 | 106 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
107 | 108 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
109 | 110 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
111 | 112 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
113 | 114 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
115 | 116 | 2 | R | 0x03 | Crv/2/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
117 | 117 | 1 | R | 0x03 | Crv/2/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
118 | 119 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
120 | 121 | 2 | R | 0x03 | Crv/2/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
122 | 123 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
124 | 125 | 2 | R | 0x03 | Crv/2/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
126 | 127 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
128 | 129 | 2 | R | 0x03 | Crv/2/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
130 | 131 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
132 | 133 | 2 | R | 0x03 | Crv/2/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
134 | 135 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
136 | 137 | 2 | R | 0x03 | Crv/2/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
138 | 138 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
139 | 139 | 1 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
140 | 141 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
142 | 143 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
144 | 145 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
146 | 147 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
148 | 149 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
150 | 151 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
152 | 153 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
154 | 155 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
156 | 157 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
158 | 159 | 2 | RW | 0x03 0x06 0x10 | Crv/3/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
160 | 160 | 1 | R | 0x03 | Crv/3/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
161 | 162 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
163 | 164 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
165 | 166 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
167 | 168 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
169 | 170 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
171 | 172 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
173 | 174 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
175 | 176 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
177 | 178 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
179 | 180 | 2 | R | 0x03 | Crv/3/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
181 | 181 | 1 | R | 0x03 | Crv/3/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
182 | 183 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
184 | 185 | 2 | R | 0x03 | Crv/3/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
186 | 187 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
188 | 189 | 2 | R | 0x03 | Crv/3/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
190 | 191 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
192 | 193 | 2 | R | 0x03 | Crv/3/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
194 | 195 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
196 | 197 | 2 | R | 0x03 | Crv/3/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
198 | 199 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
200 | 201 | 2 | R | 0x03 | Crv/3/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
202 | 202 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
203 | 203 | 1 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/ActPt | Number of active points in must trip curve. | uint16 |  |  | 5
204 | 205 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
206 | 207 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
208 | 209 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
210 | 211 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
212 | 213 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
214 | 215 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
216 | 217 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
218 | 219 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
220 | 221 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | 45 to 66 * *Actual range may vary based on inverter configuration or country setup
222 | 223 | 2 | RW | 0x03 0x06 0x10 | Crv/4/MustTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | 0 to 1000 * *Actual range may vary based on inverter configuration or country setup
224 | 224 | 1 | R | 0x03 | Crv/4/MayTrip/ActPt | Number of active points in may trip curve. | uint16 |  |  | not supported
225 | 226 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
227 | 228 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
229 | 230 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
231 | 232 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
233 | 234 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
235 | 236 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
237 | 238 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
239 | 240 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
241 | 242 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
243 | 244 | 2 | R | 0x03 | Crv/4/MayTrip/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
245 | 245 | 1 | R | 0x03 | Crv/4/MomCess/ActPt | Number of active points in the momentary cessation curve. | uint16 |  |  | not supported
246 | 247 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
248 | 249 | 2 | R | 0x03 | Crv/4/MomCess/Pt/1/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
250 | 251 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
252 | 253 | 2 | R | 0x03 | Crv/4/MomCess/Pt/2/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
254 | 255 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
256 | 257 | 2 | R | 0x03 | Crv/4/MomCess/Pt/3/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
258 | 259 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
260 | 261 | 2 | R | 0x03 | Crv/4/MomCess/Pt/4/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported
262 | 263 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Hz | Curve frequency point. | uint32 | Hz | Hz_SF | not supported
264 | 265 | 2 | R | 0x03 | Crv/4/MomCess/Pt/5/Tms | Curve time point in seconds. | uint32 | Secs | Tms_SF | not supported

## DERFreqDroop (711)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERFreqDroop (711) | uint16 |  |  | 711
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERFreqDroop (711) | uint16 | Registers |  | 52
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Frequency-Watt (Frequency-Droop) control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCtlReq | Set active control. 0 = No active control. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCtlRslt | Result of last set active control operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NCtl | Number of stored controls supported. | uint16 |  |  | 4
7 | 8 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
9 | 10 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
11 | 11 | 1 | RW | 0x03 0x06 0x10 | RvrtCtl | Default control after reversion timeout. | uint16 |  |  | 2 to 4
12 | 12 | 1 | R | 0x03 | Db_SF | Deadband scale factor. | sunssf |  |  | -3
13 | 13 | 1 | R | 0x03 | K_SF | Frequency change scale factor. | sunssf |  |  | -3
14 | 14 | 1 | R | 0x03 | RspTms_SF | Open loop response time scale factor. | sunssf |  |  | -2
15 | 16 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
17 | 18 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Ctl/1/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
21 | 22 | 2 | RW | 0x03 0x06 0x10 | Ctl/1/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | R | 0x03 | Ctl/1/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
24 | 24 | 1 | R | 0x03 | Ctl/1/ReadOnly | Control read-write access. | enum16 |  |  | 1 (R)
25 | 26 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
27 | 28 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Ctl/2/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
31 | 32 | 2 | RW | 0x03 0x06 0x10 | Ctl/2/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
33 | 33 | 1 | R | 0x03 | Ctl/2/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
34 | 34 | 1 | R | 0x03 | Ctl/2/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
35 | 36 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
37 | 38 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Ctl/3/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
41 | 42 | 2 | RW | 0x03 0x06 0x10 | Ctl/3/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | R | 0x03 | Ctl/3/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
44 | 44 | 1 | R | 0x03 | Ctl/3/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)
45 | 46 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbOf | The deadband value for over-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 6 * *Actual range may vary based on inverter configuration or country setup
47 | 48 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/DbUf | The deadband value for under-frequency conditions in Hz. | uint32 | Hz | Db_SF | 0 to 15 * *Actual range may vary based on inverter configuration or country setup
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KOf | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.006 to 65.534 * *Actual range may vary based on inverter configuration or country setup
50 | 50 | 1 | RW | 0x03 0x06 0x10 | Ctl/4/KUf | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change. | uint16 |  | K_SF | 0.017 to 65.534 * *Actual range may vary based on inverter configuration or country setup
51 | 52 | 2 | RW | 0x03 0x06 0x10 | Ctl/4/RspTms | The open-loop response time in seconds. | uint32 | Secs | RspTms_SF | 0 to 138 * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | R | 0x03 | Ctl/4/PMin | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control. | int16 | Pct |  | not supported
54 | 54 | 1 | R | 0x03 | Ctl/4/ReadOnly | Control read-write access. | enum16 |  |  | 0 (RW)

## DERWattVar (712)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERWattVar (712) | uint16 |  |  | 712
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERWattVar (712) | uint16 | Registers |  | 76
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Ena | DER Watt-Var control enable. | enum16 |  |  | 0: Disabled 1: Enabled
4 | 4 | 1 | RW | 0x03 0x06 0x10 | AdptCrvReq | Set active curve. 0 = No active curve. | uint16 |  |  | 2 to 4
5 | 5 | 1 | R | 0x03 | AdptCrvRslt | Result of last set active curve operation. | enum16 |  |  | 0: In Progress 1: Completed 2: Failed
6 | 6 | 1 | R | 0x03 | NPt | Number of curve points supported. | uint16 |  |  | 6
7 | 7 | 1 | R | 0x03 | NCrv | Number of stored curves supported. | uint16 |  |  | 4
8 | 9 | 2 | RW | 0x03 0x06 0x10 | RvrtTms | Reversion time in seconds. 0 = No reversion time. | uint32 | Secs |  | 0 to 4294967294
10 | 11 | 2 | R | 0x03 | RvrtRem | Reversion time remaining in seconds. | uint32 | Secs |  | 0 to 4294967294
12 | 12 | 1 | RW | 0x03 0x06 0x10 | RvrtCrv | Default curve after reversion timeout. | uint16 |  |  | 2 to 4
13 | 13 | 1 | R | 0x03 | W_SF | Scale factor for curve active power points. | sunssf |  |  | -2
14 | 14 | 1 | R | 0x03 | DeptRef_SF | Scale factor for curve var points. | sunssf |  |  | -2
15 | 15 | 1 | RW | 0x03 0x06 0x10 | Crv/1/ActPt | Number of active points. | uint16 |  |  | 6
16 | 16 | 1 | RW | 0x03 0x06 0x10 | Crv/1/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
17 | 17 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pri | Power priority. | enum16 |  |  | 1
18 | 18 | 1 | R | 0x03 | Crv/1/ReadOnly | Curve read-write access. | enum16 |  |  | 1 (R)
19 | 19 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
20 | 20 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
21 | 21 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
22 | 22 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
23 | 23 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
24 | 24 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
25 | 25 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
26 | 26 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
27 | 27 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
28 | 28 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
29 | 29 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
30 | 30 | 1 | RW | 0x03 0x06 0x10 | Crv/1/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
31 | 31 | 1 | RW | 0x03 0x06 0x10 | Crv/2/ActPt | Number of active points. | uint16 |  |  | 6
32 | 32 | 1 | RW | 0x03 0x06 0x10 | Crv/2/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
33 | 33 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pri | Power priority. | enum16 |  |  | 1
34 | 34 | 1 | R | 0x03 | Crv/2/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
35 | 35 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
36 | 36 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
37 | 37 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
38 | 38 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
39 | 39 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
40 | 40 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
41 | 41 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
42 | 42 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
43 | 43 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
44 | 44 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
45 | 45 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
46 | 46 | 1 | RW | 0x03 0x06 0x10 | Crv/2/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
47 | 47 | 1 | RW | 0x03 0x06 0x10 | Crv/3/ActPt | Number of active points. | uint16 |  |  | 6
48 | 48 | 1 | RW | 0x03 0x06 0x10 | Crv/3/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
49 | 49 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pri | Power priority. | enum16 |  |  | 1
50 | 50 | 1 | R | 0x03 | Crv/3/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
51 | 51 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
52 | 52 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
53 | 53 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
54 | 54 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
55 | 55 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
56 | 56 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
57 | 57 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
58 | 58 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
59 | 59 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
60 | 60 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
61 | 61 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
62 | 62 | 1 | RW | 0x03 0x06 0x10 | Crv/3/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
63 | 63 | 1 | RW | 0x03 0x06 0x10 | Crv/4/ActPt | Number of active points. | uint16 |  |  | 6
64 | 64 | 1 | RW | 0x03 0x06 0x10 | Crv/4/DeptRef | Curve dependent reference. | enum16 |  |  | 0 to 3
65 | 65 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pri | Power priority. | enum16 |  |  | 1
66 | 66 | 1 | R | 0x03 | Crv/4/ReadOnly | Curve read-write access. | enum16 |  |  | 0 (RW)
67 | 67 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
68 | 68 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/1/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
69 | 69 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
70 | 70 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/2/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
71 | 71 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | -100% to 0% * *Actual range may vary based on inverter configuration or country setup
72 | 72 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/3/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
73 | 73 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
74 | 74 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/4/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
75 | 75 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
76 | 76 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/5/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup
77 | 77 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/W | Curve active power point as percentage. | int16 | WMaxPct | W_SF | 0% to 100% * *Actual range may vary based on inverter configuration or country setup
78 | 78 | 1 | RW | 0x03 0x06 0x10 | Crv/4/Pt/6/Var | Curve reactive power point as set in DeptRef point. | int16 | VarPct | DeptRef_SF | -60% to 60% * *Actual range may vary based on inverter configuration or country setup

## DERStorageCapacity (713)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model DERStorageCapacity (713) | uint16 |  |  | 713
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model DERStorageCapacity (713) | uint16 | Registers |  | 7
3 | 3 | 1 | R | 0x03 | WHRtg | Energy rating of the DER storage. | uint16 | WH | WH_SF | not supported
4 | 4 | 1 | R | 0x03 | WHAvail | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) | uint16 | WH | WH_SF | not supported
5 | 5 | 1 | R | 0x03 | SoC | State of charge of the DER storage. | uint16 | Pct | Pct_SF | 0% to 100%
6 | 6 | 1 | R | 0x03 | SoH | State of health of the DER storage. | uint16 | Pct | Pct_SF | not supported
7 | 7 | 1 | R | 0x03 | Sta | Storage status. | enum16 |  |  | not supported
8 | 8 | 1 | R | 0x03 | WH_SF | Scale factor for energy capacity. | sunssf |  |  | not supported
9 | 9 | 1 | R | 0x03 | Pct_SF | Scale factor for percentage. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0